## 0
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165800 | 4489300 | 4489300
2 | Auxiliary power consumption | kWhr | 17741 | 517714 | 517714
3 | Net Power Exported | kWhr | 148059 | 3971586 | 3971586
4 | Auxiliary power consumption | ( % ) | 10.7002 | 11.5322 | 11.5322
5 | Average Power Generation | MWhr | 6.9083 | 6.389 | 6.389
6 | Plant Running Hours | Hrs | 24 | 702.66 | 702.66
6 | PLF | ( % ) | 69.0833 | 63.8901 | 63.8901
7 | Feed Water consumption | MT | 762 | 21099 | 21099
8 | Boiler Steam Generation | MT | 740 | 20494 | 20494
9 | Bleed steam | MT | 61 | 1192 | 1192
10 | Turbine steam consumption | MT | 693 | 18677 | 18677
11 | Condensate Generation | MT | 538 | 15181 | 15181
12 | Auxilairy steam consumption | MT | 17 | 528 | 528
13 | Specific steam consumption | Kg/Kwhr | 4.1797 | 4.1603 | 4.1603
14 | Specific fuel consumption | Kg/Kwhr | 0.79011 | 0.86183 | 0.86183
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2815.4946 | 2803.2814 | 2803.2814
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3850.948 | 3938.842 | 3938.842
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 131 | 3869 | 3869
2 | GCV ( ADB ) | Kcal/kg | 4849
WTP Report
1 | DM water Generation | m3 | 13 | 490 | 490
2 | DM water Consumption | m3 | 14 | 505 | 505
3 | CT Makeup Water Consumption | m3 | 18 | 538 | 538
4 | Fly ash combustible/ GCV | % / kcal/kg | 26 | 1971
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 37 | 632 | 632
6 | Fly ash to Coalyard(Truck) | nos | 0 | 66 | 66
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 1
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-01 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 103100 | 103100 | 4592400
2 | Auxiliary power consumption | kWhr | 16407 | 16407 | 534121
3 | Net Power Exported | kWhr | 86693 | 86693 | 4058279
4 | Auxiliary power consumption | ( % ) | 15.9137 | 15.9137 | 11.6305
5 | Average Power Generation | MWhr | 4.2958 | 4.2958 | 6.3199
6 | Plant Running Hours | Hrs | 24 | 24 | 726.66
6 | PLF | ( % ) | 42.9583 | 42.9583 | 63.1987
7 | Feed Water consumption | MT | 558 | 558 | 21657
8 | Boiler Steam Generation | MT | 542 | 542 | 21036
9 | Bleed steam | MT | 7 | 7 | 1199
10 | Turbine steam consumption | MT | 434 | 434 | 19111
11 | Condensate Generation | MT | 382 | 382 | 15563
12 | Auxilairy steam consumption | MT | 18 | 18 | 546
13 | Specific steam consumption | Kg/Kwhr | 4.2095 | 4.2095 | 4.1614
14 | Specific fuel consumption | Kg/Kwhr | 0.93113 | 0.93113 | 0.86338
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2838.2347 | 2838.2347 | 2804.0661
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4535.8751 | 4535.8751 | 3952.2455
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 96 | 96 | 3965
2 | GCV ( ADB ) | Kcal/kg | 4825
WTP Report
1 | DM water Generation | m2 | 19 | 19 | 509
2 | DM water Consumption | m3 | 18 | 18 | 523
3 | CT Makeup Water Consumption | m3 | 15 | 15 | 553
4 | Fly ash combustible/ GCV | % / kcal/kg | 24 | 1820
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 20 | 652
6 | Fly ash to Coal yard(Truck) | nos | 1 | 1 | 67
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 2
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-02 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 156500 | 259600 | 4748900
2 | Auxiliary power consumption | kWhr | 17325 | 33732 | 551446
3 | Net Power Exported | kWhr | 139175 | 225868 | 4197454
4 | Auxiliary power consumption | ( % ) | 11.0703 | 12.9938 | 11.6121
5 | Average Power Generation | MWhr | 6.5208 | 5.4083 | 6.3263
6 | Plant Running Hours | Hrs | 24 | 48 | 750.66
7 | PLF | ( % ) | 65.2083 | 54.0833 | 63.263
8 | Feed Water consumption | MT | 733 | 1291 | 22390
9 | Boiler Steam Generation | MT | 710 | 1252 | 21746
10 | Bleed steam | MT | 41 | 48 | 1240
11 | Turbine steam consumption | MT | 645 | 1079 | 19756
12 | Condensate Generation | MT | 522 | 904 | 16085
13 | Auxilairy steam consumption | MT | 18 | 36 | 564
14 | Specific steam consumption | Kg/Kwhr | 4.1214 | 4.1564 | 4.1601
15 | Specific fuel consumption | Kg/Kwhr | 0.86262 | 0.88983 | 0.86336
16 | Heat Rate(TG)2880 | Kcal/Kwh | 2776.7732 | 2801.1826 | 2803.1666
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3914.3934 | 4161.2145 | 3950.9981
18 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 135 | 231 | 4100
2 | GCV ( ADB ) | Kcal/kg | 4511
WTP Report
1 | DM water Generation | m3 | 19 | 38 | 528
2 | DM water Consumption | m3 | 16 | 34 | 539
3 | CT Makeup Water Consumption | m3 | 14 | 29 | 567
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1730
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 35 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 1 | 2 | 68
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 3
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-03 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 161600 | 421200 | 4910500
2 | Auxiliary power consumption | kWhr | 17500 | 51232 | 568946
3 | Net Power Exported | kWhr | 144100 | 369968 | 4341554
4 | Auxiliary power consumption | ( % ) | 10.8292 | 12.1633 | 11.5863
5 | Average Power Generation | MWhr | 6.7333 | 5.85 | 6.3389
6 | Plant Running Hours | Hrs | 24 | 72 | 774.66
6 | PLF | ( % ) | 67.3333 | 58.5 | 63.3891
7 | Feed Water consumption | MT | 741 | 2032 | 23131
8 | Boiler Steam Generation | MT | 725 | 1977 | 22471
9 | Bleed steam | MT | 56 | 104 | 1296
10 | Turbine steam consumption | MT | 673 | 1752 | 20429
11 | Condensate Generation | MT | 524 | 1428 | 16609
12 | Auxilairy steam consumption | MT | 18 | 54 | 582
13 | Specific steam consumption | Kg/Kwhr | 4.1646 | 4.1595 | 4.1603
14 | Specific fuel consumption | Kg/Kwhr | 0.89109 | 0.89031 | 0.86427
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.1918 | 2802.7208 | 2803.2333
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3870.946 | 4049.8484 | 3948.3637
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 144 | 375 | 4244
2 | GCV ( ADB ) | Kcal/kg | 4328
WTP Report
1 | DM water Generation | m3 | 13 | 51 | 541
2 | DM water Consumption | m3 | 13 | 47 | 552
3 | CT Makeup Water Consumption | m3 | 18 | 47 | 585
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1611
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 5 | 7 | 73
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 4
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-04 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 151600 | 572800 | 5062100
2 | Auxiliary power consumption | kWhr | 17268 | 68500 | 586214
3 | Net Power Exported | kWhr | 134332 | 504300 | 4475886
4 | Auxiliary power consumption | ( % ) | 11.3905 | 11.9588 | 11.5805
5 | Average Power Generation | MWhr | 6.3167 | 5.9667 | 6.3382
6 | Plant Running Hours | Hrs | 24 | 96 | 798.66
6 | PLF | ( % ) | 63.1667 | 59.6667 | 63.3824
7 | Feed Water consumption | MT | 706 | 2738 | 23837
8 | Boiler Steam Generation | MT | 681 | 2658 | 23152
9 | Bleed steam | MT | 51 | 155 | 1347
10 | Turbine steam consumption | MT | 636 | 2388 | 21065
11 | Condensate Generation | MT | 499 | 1927 | 17108
12 | Auxilairy steam consumption | MT | 18 | 72 | 600
13 | Specific steam consumption | Kg/Kwhr | 4.1953 | 4.169 | 4.1613
14 | Specific fuel consumption | Kg/Kwhr | 0.81135 | 0.86941 | 0.86269
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2826.1741 | 2808.9281 | 2803.9203
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3875.8626 | 4003.8005 | 3946.1924
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 123 | 498 | 4367
2 | GCV ( ADB ) | Kcal/kg | 4752
WTP Report
1 | DM water Generation | m3 | 13 | 64 | 554
2 | DM water Consumption | m3 | 14 | 61 | 566
3 | CT Makeup Water Consumption | m3 | 26 | 73 | 611
4 | Fly ash combustible/ GCV | % / kcal/kg | 23.89 | 1752
5 | Fly ash to cement mill | MT | 0 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 4 | 11 | 77
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 5
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-05 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 147300 | 720100 | 5209400
2 | Auxiliary power consumption | kWhr | 17252 | 85752 | 603466
3 | Net Power Exported | kWhr | 130048 | 634348 | 4605934
4 | Auxiliary power consumption | ( % ) | 11.7122 | 11.9083 | 11.5842
5 | Average Power Generation | MWhr | 6.1375 | 6.0008 | 6.3324
6 | Plant Running Hours | Hrs | 24 | 120 | 822.66
6 | PLF | ( % ) | 61.375 | 60.0083 | 63.3239
7 | Feed Water consumption | MT | 690 | 3428 | 24527
8 | Boiler Steam Generation | MT | 670 | 3328 | 23822
9 | Bleed steam | MT | 49 | 204 | 1396
10 | Turbine steam consumption | MT | 619 | 3007 | 21684
11 | Condensate Generation | MT | 485 | 2412 | 17593
12 | Auxilairy steam consumption | MT | 18 | 90 | 618
13 | Specific steam consumption | Kg/Kwhr | 4.2023 | 4.1758 | 4.1625
14 | Specific fuel consumption | Kg/Kwhr | 0.81466 | 0.85821 | 0.86133
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2831.2084 | 2813.4856 | 2804.6919
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3924.574 | 3987.5943 | 3945.5811
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 120 | 618 | 4487
2 | GCV ( ADB ) | Kcal/kg | 4777
WTP Report
1 | DM water Generation | m3 | 16 | 80 | 570
2 | DM water Consumption | m3 | 15 | 76 | 581
3 | CT Makeup Water Consumption | m3 | 17 | 90 | 628
4 | Fly ash combustible/ GCV | % / kcal/kg | 25 | 1754
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 5 | 16 | 82
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 6
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-06 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 153000 | 873100 | 5362400
2 | Auxiliary power consumption | kWhr | 17283 | 103035 | 620749
3 | Net Power Exported | kWhr | 135717 | 770065 | 4741651
4 | Auxiliary power consumption | ( % ) | 11.2961 | 11.8011 | 11.576
5 | Average Power Generation | MWhr | 6.375 | 6.0632 | 6.3336
6 | Plant Running Hours | Hrs | 24 | 144 | 846.66
6 | PLF | ( % ) | 63.75 | 60.6319 | 63.3359
7 | Feed Water consumption | MT | 704 | 4132 | 25231
8 | Boiler Steam Generation | MT | 690 | 4018 | 24512
9 | Bleed steam | MT | 51 | 255 | 1447
10 | Turbine steam consumption | MT | 636 | 3643 | 22320
11 | Condensate Generation | MT | 497 | 2909 | 18090
12 | Auxilairy steam consumption | MT | 17 | 107 | 635
13 | Specific steam consumption | Kg/Kwhr | 4.1569 | 4.1725 | 4.1623
14 | Specific fuel consumption | Kg/Kwhr | 0.81046 | 0.84985 | 0.85988
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2800.3137 | 2811.1774 | 2804.567
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3891.1513 | 3970.6939 | 3944.0281
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 124 | 742 | 4611
2 | GCV ( ADB ) | Kcal/kg | 4806
WTP Report
1 | DM water Generation | m3 | 13 | 93 | 583
2 | DM water Consumption | m3 | 14 | 90 | 595
3 | CT Makeup Water Consumption | m3 | 17 | 107 | 645
4 | Fly ash combustible/ GCV | % / kcal/kg | 23 | 1672
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 5 | 21 | 87
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 7
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-07 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 135200 | 1008300 | 5497600
2 | Auxiliary power consumption | kWhr | 16790 | 119825 | 637539
3 | Net Power Exported | kWhr | 118410 | 888475 | 4860061
4 | Auxiliary power consumption | ( % ) | 12.4186 | 11.8839 | 11.5967
5 | Average Power Generation | MWhr | 5.6333 | 6.0018 | 6.3143
6 | Plant Running Hours | Hrs | 24 | 168 | 870.66
6 | PLF | ( % ) | 56.3333 | 60.0179 | 63.1429
7 | Feed Water consumption | MT | 657 | 4789 | 25888
8 | Boiler Steam Generation | MT | 640 | 4658 | 25152
9 | Bleed steam | MT | 29 | 284 | 1476
10 | Turbine steam consumption | MT | 566 | 4209 | 22886
11 | Condensate Generation | MT | 462 | 3371 | 18552
12 | Auxilairy steam consumption | MT | 19 | 126 | 654
13 | Specific steam consumption | Kg/Kwhr | 4.1864 | 4.1744 | 4.1629
14 | Specific fuel consumption | Kg/Kwhr | 0.8432 | 0.84895 | 0.85947
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2820.3254 | 2812.404 | 2804.9545
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4084.3575 | 3985.9347 | 3947.4792
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 114 | 856 | 4725
2 | GCV ( ADB ) | Kcal/kg | 4825
1 | DM water Generation | m3 | 12 | 105 | 595
2 | DM water Consumption | m3 | 13 | 103 | 608
3 | CT Makeup Water Consumption | m3 | 16 | 123 | 661
4 | Fly ash combustible/ GCV | % / kcal/kg | 24 | 1820
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 55 | 687
6 | Fly ash to Coal yard(Truck) | nos | 4 | 25 | 91
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 8
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-08 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 139900 | 1148200 | 5637500
2 | Auxiliary power consumption | kWhr | 16949 | 136774 | 654488
3 | Net Power Exported | kWhr | 122951 | 1011426 | 4983012
4 | Auxiliary power consumption | ( % ) | 12.1151 | 11.912 | 11.6095
5 | Average Power Generation | MWhr | 5.8292 | 5.9802 | 6.3013
6 | Plant Running Hours | Hrs | 24 | 192 | 894.66
6 | PLF | ( % ) | 58.2917 | 59.8021 | 63.0128
7 | Feed Water consumption | MT | 692 | 5481 | 26580
8 | Boiler Steam Generation | MT | 670 | 5328 | 25822
9 | Bleed steam | MT | 9 | 293 | 1485
10 | Turbine steam consumption | MT | 569 | 4778 | 23455
11 | Condensate Generation | MT | 492 | 3863 | 19044
12 | Auxilairy steam consumption | MT | 17 | 143 | 671
13 | Specific steam consumption | Kg/Kwhr | 4.0672 | 4.1613 | 4.1605
14 | Specific fuel consumption | Kg/Kwhr | 0.85776 | 0.85003 | 0.85942
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2739.7927 | 2803.5569 | 2803.3375
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4132.164 | 4003.7517 | 3952.0623
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 120 | 976 | 4845
2 | GCV ( ADB ) | Kcal/kg | 4755
WTP Report
1 | DM water Generation | m3 | 13 | 118 | 608
2 | DM water Consumption | m3 | 12 | 115 | 620
3 | CT Makeup Water Consumption | m3 | 17 | 140 | 678
4 | Fly ash combustible/ GCV | % / kcal/kg | 25 | 1776
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 80 | 712
6 | Fly ash to Coal yard(Truck) | nos | 1 | 26 | 92
7 | Fly ash to Dumpyard(Truck) | nos |  | 0 | 0

## 9
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-09 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 133200 | 1281400 | 5770700
2 | Auxiliary power consumption | kWhr | 17083 | 153857 | 671571
3 | Net Power Exported | kWhr | 116117 | 1127543 | 5099129
4 | Auxiliary power consumption | ( % ) | 12.8251 | 12.0069 | 11.6376
5 | Average Power Generation | MWhr | 5.55 | 5.9324 | 6.2816
6 | Plant Running Hours | Hrs | 24 | 216 | 918.66
6 | PLF | ( % ) | 55.5 | 59.3241 | 62.8165
7 | Feed Water consumption | MT | 662 | 6143 | 27242
8 | Boiler Steam Generation | MT | 636 | 5964 | 26458
9 | Bleed steam | MT | 11 | 304 | 1496
10 | Turbine steam consumption | MT | 542 | 5320 | 23997
11 | Condensate Generation | MT | 466 | 4329 | 19510
12 | Auxilairy steam consumption | MT | 18 | 161 | 689
13 | Specific steam consumption | Kg/Kwhr | 4.0691 | 4.1517 | 4.1584
14 | Specific fuel consumption | Kg/Kwhr | 0.97598 | 0.86312 | 0.86211
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2742.0871 | 2797.1672 | 2801.9237
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4119.7736 | 4015.812 | 3955.9334
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 130 | 1106 | 4975
2 | GCV ( ADB ) | Kcal/kg | 4067
WTP Report
1 | DM water Generation | m3 | 15 | 133 | 623
2 | DM water Consumption | m3 | 16 | 131 | 636
3 | CT Makeup Water Consumption | m3 | 17 | 157 | 695
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1581
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 44 | 124 | 756
6 | Fly ash to Coal yard(Truck) | nos | 0 | 26 | 92
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 10
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-10 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 141900 | 1423300 | 5912600
2 | Auxiliary power consumption | kWhr | 17074 | 170931 | 688645
3 | Net Power Exported | kWhr | 124826 | 1252369 | 5223955
4 | Auxiliary power consumption | ( % ) | 12.0324 | 12.0095 | 11.6471
5 | Average Power Generation | MWhr | 5.9125 | 5.9304 | 6.2723
6 | Plant Running Hours | Hrs | 24 | 240 | 942.66
6 | PLF | ( % ) | 59.125 | 59.3042 | 62.7225
7 | Feed Water consumption | MT | 688 | 6831 | 27930
8 | Boiler Steam Generation | MT | 670 | 6634 | 27128
9 | Bleed steam | MT | 18 | 322 | 1514
10 | Turbine steam consumption | MT | 581 | 5901 | 24578
11 | Condensate Generation | MT | 488 | 4817 | 19998
12 | Auxilairy steam consumption | MT | 18 | 179 | 707
13 | Specific steam consumption | Kg/Kwhr | 4.0944 | 4.146 | 4.1569
14 | Specific fuel consumption | Kg/Kwhr | 0.98661 | 0.87543 | 0.8651
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2758.7245 | 2793.3345 | 2800.8869
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4073.9235 | 4021.6056 | 3958.7652
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 1246 | 5115
2 | GCV ( ADB ) | Kcal/kg | 4109
WTP Report
1 | DM water Generation | m3 | 17 | 150 | 640
2 | DM water Consumption | m3 | 15 | 146 | 651
3 | CT Makeup Water Consumption | m3 | 38 | 195 | 733
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1502
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 124 | 756
6 | Fly ash to Coal yard(Truck) | nos | 5 | 31 | 97
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 11
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-11 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 134900 | 1558200 | 6047500
2 | Auxiliary power consumption | kWhr | 17357 | 188288 | 706002
3 | Net Power Exported | kWhr | 117543 | 1369912 | 5341498
4 | Auxiliary power consumption | ( % ) | 12.8666 | 12.0837 | 11.6743
5 | Average Power Generation | MWhr | 5.6208 | 5.9023 | 6.2561
6 | Plant Running Hours | Hrs | 24 | 264 | 966.66
6 | PLF | ( % ) | 56.2083 | 59.0227 | 62.5608
7 | Feed Water consumption | MT | 680 | 7511 | 28610
8 | Boiler Steam Generation | MT | 660 | 7294 | 27788
9 | Bleed steam | MT | 0 | 322 | 1514
10 | Turbine steam consumption | MT | 547 | 6448 | 25125
11 | Condensate Generation | MT | 481 | 5298 | 20479
12 | Auxilairy steam consumption | MT | 18 | 197 | 725
13 | Specific steam consumption | Kg/Kwhr | 4.0549 | 4.1381 | 4.1546
14 | Specific fuel consumption | Kg/Kwhr | 1.023 | 0.8882 | 0.86862
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2733.1431 | 2788.1235 | 2799.3758
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4221.3606 | 4038.8993 | 3964.6228
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 1384 | 5253
2 | GCV ( ADB ) | Kcal/kg | 4122
WTP Report
1 | DM water Generation | m3 | 19 | 169 | 659
2 | DM water Consumption | m3 | 19 | 165 | 670
3 | CT Makeup Water Consumption | m3 | 20 | 215 | 753
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.8 | 1425
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 15 | 139 | 771
6 | Fly ash to Coal yard(Truck) | nos | 3 | 34 | 100
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 12
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-12 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 140000 | 1698200 | 6187500
2 | Auxiliary power consumption | kWhr | 17149 | 205437 | 723151
3 | Net Power Exported | kWhr | 122851 | 1492763 | 5464349
4 | Auxiliary power consumption | ( % ) | 12.2493 | 12.0973 | 11.6873
5 | Average Power Generation | MWhr | 5.8333 | 5.8965 | 6.2458
6 | Plant Running Hours | Hrs | 24 | 288 | 990.66
6 | PLF | ( % ) | 58.3333 | 58.9653 | 62.4584
7 | Feed Water consumption | MT | 698 | 8209 | 29308
8 | Boiler Steam Generation | MT | 672 | 7966 | 28460
9 | Bleed steam | MT | 0 | 322 | 1514
10 | Turbine steam consumption | MT | 567 | 7015 | 25692
11 | Condensate Generation | MT | 499 | 5797 | 20978
12 | Auxilairy steam consumption | MT | 18 | 215 | 743
13 | Specific steam consumption | Kg/Kwhr | 4.05 | 4.1308 | 4.1522
14 | Specific fuel consumption | Kg/Kwhr | 0.98571 | 0.89624 | 0.87127
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2728.8643 | 2783.2381 | 2797.7804
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4141.5385 | 4047.3609 | 3968.6257
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 1522 | 5391
2 | GCV ( ADB ) | Kcal/kg | 4089
WTP Report
1 | DM water Generation | m3 | 14 | 183 | 673
2 | DM water Consumption | m3 | 15 | 180 | 685
3 | CT Makeup Water Consumption | m3 | 17 | 232 | 770
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1380
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 49 | 188 | 820
6 | Fly ash to Coal yard(Truck) | nos | 0 | 34 | 100
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 13
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-13 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 146600 | 1844800 | 6334100
2 | Auxiliary power consumption | kWhr | 17460 | 222897 | 740611
3 | Net Power Exported | kWhr | 129140 | 1621903 | 5593489
4 | Auxiliary power consumption | ( % ) | 11.91 | 12.0824 | 11.6924
5 | Average Power Generation | MWhr | 6.1083 | 5.9128 | 6.2426
6 | Plant Running Hours | Hrs | 24 | 312 | 1014.66
6 | PLF | ( % ) | 61.0833 | 59.1282 | 62.4258
7 | Feed Water consumption | MT | 723 | 8932 | 30031
8 | Boiler Steam Generation | MT | 693 | 8659 | 29153
9 | Bleed steam | MT | 0 | 322 | 1514
10 | Turbine steam consumption | MT | 591 | 7606 | 26283
11 | Condensate Generation | MT | 517 | 6314 | 21495
12 | Auxilairy steam consumption | MT | 17 | 232 | 760
13 | Specific steam consumption | Kg/Kwhr | 4.0314 | 4.1229 | 4.1494
14 | Specific fuel consumption | Kg/Kwhr | 0.96862 | 0.90199 | 0.87353
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2715.9823 | 2777.8935 | 2795.8872
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4078.6809 | 4049.8498 | 3971.1729
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 142 | 1664 | 5533
2 | GCV ( ADB ) | Kcal/kg | 4139
WTP Report
1 | DM water Generation | m3 | 13 | 196 | 686
2 | DM water Consumption | m3 | 14 | 194 | 699
3 | CT Makeup Water Consumption | m3 | 17 | 249 | 787
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1514
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 213 | 845
6 | Fly ash to Coal yard(Truck) | nos | 3 | 37 | 103
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 14
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-14 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 143500 | 1988300 | 6477600
2 | Auxiliary power consumption | kWhr | 17394 | 240291 | 758005
3 | Net Power Exported | kWhr | 126106 | 1748009 | 5719595
4 | Auxiliary power consumption | ( % ) | 12.1213 | 12.0852 | 11.7019
5 | Average Power Generation | MWhr | 5.9792 | 5.9176 | 6.2365
6 | Plant Running Hours | Hrs | 24 | 336 | 1038.66
6 | PLF | ( % ) | 59.7917 | 59.1756 | 62.365
7 | Feed Water consumption | MT | 695 | 9627 | 30726
8 | Boiler Steam Generation | MT | 679 | 9338 | 29832
9 | Bleed steam | MT | 33 | 355 | 1547
10 | Turbine steam consumption | MT | 595 | 8201 | 26878
11 | Condensate Generation | MT | 488 | 6802 | 21983
12 | Auxilairy steam consumption | MT | 18 | 250 | 778
13 | Specific steam consumption | Kg/Kwhr | 4.1463 | 4.1246 | 4.1494
14 | Specific fuel consumption | Kg/Kwhr | 0.94774 | 0.9053 | 0.87517
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2794.0418 | 2779.059 | 2795.8463
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4082.6141 | 4052.2144 | 3973.6417
17 | DG Power Generation | kWhr |  | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 136 | 1800 | 5669
2 | GCV ( ADB ) | Kcal/kg | 4290
WTP Report
1 | DM water Generation | m3 | 18 | 214 | 704
2 | DM water Consumption | m3 | 17 | 211 | 716
3 | CT Makeup Water Consumption | m3 | 18 | 267 | 805
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1410
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 42 | 255 | 887
6 | Fly ash to Coal yard(Truck) | nos | 0 | 37 | 103
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 15
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-15 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 143000 | 2131300 | 6620600
2 | Auxiliary power consumption | kWhr | 17162 | 257453 | 775167
3 | Net Power Exported | kWhr | 125838 | 1873847 | 5845433
4 | Auxiliary power consumption | ( % ) | 12.0014 | 12.0796 | 11.7084
5 | Average Power Generation | MWhr | 5.9583 | 5.9203 | 6.2302
6 | Plant Running Hours | Hrs | 24 | 360 | 1062.66
6 | PLF | ( % ) | 59.5833 | 59.2028 | 62.3021
7 | Feed Water consumption | MT | 678 | 10305 | 31404
8 | Boiler Steam Generation | MT | 655 | 9993 | 30487
9 | Bleed steam | MT | 52 | 407 | 1599
10 | Turbine steam consumption | MT | 602 | 8803 | 27480
11 | Condensate Generation | MT | 471 | 7273 | 22454
12 | Auxilairy steam consumption | MT | 18 | 268 | 796
13 | Specific steam consumption | Kg/Kwhr | 4.2098 | 4.1303 | 4.1507
14 | Specific fuel consumption | Kg/Kwhr | 0.93007 | 0.90696 | 0.87636
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2836.5455 | 2782.9161 | 2796.7254
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3952.08 | 4045.4959 | 3973.176
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 133 | 1933 | 5802
2 | GCV ( ADB ) | Kcal/kg | 4230
WTP Report
1 | DM water Generation | m3 | 14 | 228 | 718
2 | DM water Consumption | m3 | 16 | 227 | 732
3 | CT Makeup Water Consumption | m3 | 18 | 285 | 823
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1380
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 255 | 887
6 | Fly ash to Coal yard(Truck) | nos | 4 | 41 | 107
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 16
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-16 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 159300 | 2290600 | 6779900
2 | Auxiliary power consumption | kWhr | 17434 | 274887 | 792601
3 | Net Power Exported | kWhr | 141866 | 2015713 | 5987299
4 | Auxiliary power consumption | ( % ) | 10.9441 | 12.0007 | 11.6905
5 | Average Power Generation | MWhr | 6.6375 | 5.9651 | 6.2392
6 | Plant Running Hours | Hrs | 24 | 384 | 1086.66
6 | PLF | ( % ) | 66.375 | 59.651 | 62.3921
7 | Feed Water consumption | MT | 735 | 11040 | 32139
8 | Boiler Steam Generation | MT | 725 | 10718 | 31212
9 | Bleed steam | MT | 43 | 450 | 1642
10 | Turbine steam consumption | MT | 660 | 9463 | 28140
11 | Condensate Generation | MT | 523 | 7796 | 22977
12 | Auxilairy steam consumption | MT | 18 | 286 | 814
13 | Specific steam consumption | Kg/Kwhr | 4.1431 | 4.1312 | 4.1505
14 | Specific fuel consumption | Kg/Kwhr | 0.91023 | 0.90719 | 0.87715
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2790.7721 | 2783.4624 | 2796.5855
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3926.8354 | 4037.2436 | 3972.0872
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 145 | 2078 | 5947
2 | GCV ( ADB ) | Kcal/kg | 4199
WTP Report
1 | DM water Generation | m3 | 15 | 243 | 733
2 | DM water Consumption | m3 | 13 | 240 | 745
3 | CT Makeup Water Consumption | m3 | 17 | 302 | 840
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1405
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 255 | 887
6 | Fly ash to Coal yard(Truck) | nos | 4 | 45 | 111
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 17
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-17 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 160600 | 2451200 | 6940500
2 | Auxiliary power consumption | kWhr | 17570 | 292457 | 810171
3 | Net Power Exported | kWhr | 143030 | 2158743 | 6130329
4 | Auxiliary power consumption | ( % ) | 10.9402 | 11.9312 | 11.6731
5 | Average Power Generation | MWhr | 6.6917 | 6.0078 | 6.249
6 | Plant Running Hours | Hrs | 24 | 408 | 1110.66
6 | PLF | ( % ) | 66.9167 | 60.0784 | 62.4899
7 | Feed Water consumption | MT | 743 | 11783 | 32882
8 | Boiler Steam Generation | MT | 714 | 11432 | 31926
9 | Bleed steam | MT | 48 | 498 | 1690
10 | Turbine steam consumption | MT | 672 | 10135 | 28812
11 | Condensate Generation | MT | 529 | 8325 | 23506
12 | Auxilairy steam consumption | MT | 17 | 303 | 831
13 | Specific steam consumption | Kg/Kwhr | 4.1843 | 4.1347 | 4.1513
14 | Specific fuel consumption | Kg/Kwhr | 0.90909 | 0.90731 | 0.87789
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2818.655 | 2785.7682 | 2797.0962
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3835.9517 | 4024.0552 | 3968.9371
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 146 | 2224 | 6093
2 | GCV ( ADB ) | Kcal/kg | 4192
WTP Report
1 | DM water Generation | m3 | 13 | 256 | 746
2 | DM water Consumption | m3 | 14 | 254 | 759
3 | CT Makeup Water Consumption | m3 | 17 | 319 | 857
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1429
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 275 | 907
6 | Fly ash to Coal yard(Truck) | nos | 3 | 48 | 114
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 18
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-18 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 169700 | 2620900 | 7110200
2 | Auxiliary power consumption | kWhr | 17904 | 310361 | 828075
3 | Net Power Exported | kWhr | 151796 | 2310539 | 6282125
4 | Auxiliary power consumption | ( % ) | 10.5504 | 11.8418 | 11.6463
5 | Average Power Generation | MWhr | 7.0708 | 6.0669 | 6.2664
6 | Plant Running Hours | Hrs | 24 | 432 | 1134.66
6 | PLF | ( % ) | 70.7083 | 60.669 | 62.6637
7 | Feed Water consumption | MT | 776 | 12559 | 33658
8 | Boiler Steam Generation | MT | 745 | 12177 | 32671
9 | Bleed steam | MT | 56 | 554 | 1746
10 | Turbine steam consumption | MT | 711 | 10846 | 29523
11 | Condensate Generation | MT | 557 | 8882 | 24063
12 | Auxilairy steam consumption | MT | 18 | 321 | 849
13 | Specific steam consumption | Kg/Kwhr | 4.1897 | 4.1383 | 4.1522
14 | Specific fuel consumption | Kg/Kwhr | 0.84266 | 0.90312 | 0.87705
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2821.9976 | 2788.114 | 2797.6905
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3787.8685 | 4008.7624 | 3964.6155
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 143 | 2367 | 6236
2 | GCV ( ADB ) | Kcal/kg | 4470
WTP Report
1 | DM water Generation | m3 | 14 | 270 | 760
2 | DM water Consumption | m3 | 13 | 267 | 772
3 | CT Makeup Water Consumption | m3 | 45 | 364 | 902
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1421
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 300 | 932
6 | Fly ash to Coal yard(Truck) | nos | 2 | 50 | 116
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 19
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-19 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 169400 | 2790300 | 7279600
2 | Auxiliary power consumption | kWhr | 18101 | 328462 | 846176
3 | Net Power Exported | kWhr | 151299 | 2461838 | 6433424
4 | Auxiliary power consumption | ( % ) | 10.6854 | 11.7716 | 11.6239
5 | Average Power Generation | MWhr | 7.0583 | 6.1191 | 6.2828
6 | Plant Running Hours | Hrs | 24 | 456 | 1158.66
6 | PLF | ( % ) | 70.5833 | 61.1908 | 62.8277
7 | Feed Water consumption | MT | 777 | 13336 | 34435
8 | Boiler Steam Generation | MT | 745 | 12922 | 33416
9 | Bleed steam | MT | 54 | 608 | 1800
10 | Turbine steam consumption | MT | 704 | 11550 | 30227
11 | Condensate Generation | MT | 555 | 9437 | 24618
12 | Auxilairy steam consumption | MT | 19 | 340 | 868
13 | Specific steam consumption | Kg/Kwhr | 4.1558 | 4.1393 | 4.1523
14 | Specific fuel consumption | Kg/Kwhr | 0.90319 | 0.90313 | 0.87766
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2799.7166 | 2788.8184 | 2797.7377
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3794.5766 | 3995.7591 | 3960.6586
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 153 | 2520 | 6389
2 | GCV ( ADB ) | Kcal/kg | 4180
WTP Report
1 | DM water Generation | m3 | 16 | 286 | 776
2 | DM water Consumption | m3 | 16 | 283 | 788
3 | CT Makeup Water Consumption | m3 | 20 | 384 | 922
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1380
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 320 | 952
6 | Fly ash to Coal yard(Truck) | nos | 4 | 54 | 120
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 20
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-20 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 175900 | 2966200 | 7455500
2 | Auxiliary power consumption | kWhr | 17932 | 346394 | 864108
3 | Net Power Exported | kWhr | 157968 | 2619806 | 6591392
4 | Auxiliary power consumption | ( % ) | 10.1944 | 11.678 | 11.5902
5 | Average Power Generation | MWhr | 7.3292 | 6.1796 | 6.304
6 | Plant Running Hours | Hrs | 24 | 480 | 1182.66
6 | PLF | ( % ) | 73.2917 | 61.7958 | 63.0401
7 | Feed Water consumption | MT | 797 | 14133 | 35232
8 | Boiler Steam Generation | MT | 780 | 13702 | 34196
9 | Bleed steam | MT | 59 | 667 | 1859
10 | Turbine steam consumption | MT | 733 | 12283 | 30960
11 | Condensate Generation | MT | 569 | 10006 | 25187
12 | Auxilairy steam consumption | MT | 17 | 357 | 885
13 | Specific steam consumption | Kg/Kwhr | 4.1671 | 4.141 | 4.1526
14 | Specific fuel consumption | Kg/Kwhr | 0.8755 | 0.90149 | 0.87761
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.7027 | 2789.879 | 2797.9492
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3826.0375 | 3985.6944 | 3957.4824
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 154 | 2674 | 6543
2 | GCV ( ADB ) | Kcal/kg | 4322
WTP Report
1 | DM water Generation | m3 | 12 | 298 | 788
2 | DM water Consumption | m3 | 13 | 296 | 801
3 | CT Makeup Water Consumption | m3 | 20 | 404 | 942
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1413
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 340 | 972
6 | Fly ash to Coal yard(Truck) | nos | 4 | 58 | 124
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 21
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-21 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176800 | 3143000 | 7632300
2 | Auxiliary power consumption | kWhr | 18003 | 364397 | 882111
3 | Net Power Exported | kWhr | 158797 | 2778603 | 6750189
4 | Auxiliary power consumption | ( % ) | 10.1827 | 11.5939 | 11.5576
5 | Average Power Generation | MWhr | 7.3667 | 6.2361 | 6.3251
6 | Plant Running Hours | Hrs | 24 | 504 | 1206.66
6 | PLF | ( % ) | 73.6667 | 62.3611 | 63.2515
7 | Feed Water consumption | MT | 806 | 14939 | 36038
8 | Boiler Steam Generation | MT | 786 | 14488 | 34982
9 | Bleed steam | MT | 60 | 727 | 1919
10 | Turbine steam consumption | MT | 740 | 13023 | 31700
11 | Condensate Generation | MT | 577 | 10583 | 25764
12 | Auxilairy steam consumption | MT | 18 | 375 | 903
13 | Specific steam consumption | Kg/Kwhr | 4.1855 | 4.1435 | 4.1534
14 | Specific fuel consumption | Kg/Kwhr | 0.87104 | 0.89978 | 0.87746
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2819.4005 | 2791.5396 | 2798.4461
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3835.8423 | 3977.2649 | 3954.6647
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 154 | 2828 | 6697
2 | GCV ( ADB ) | Kcal/kg | 4402
1 | DM water Generation | m3 | 17 | 315 | 805
2 | DM water Consumption | m3 | 15 | 311 | 816
3 | CT Makeup Water Consumption | m3 | 16 | 420 | 958
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1533
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 360 | 992
6 | Fly ash to Coal yard(Truck) | nos | 4 | 62 | 128
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 22
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-22 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 157500 | 3300500 | 7789800
2 | Auxiliary power consumption | kWhr | 17586 | 381983 | 899697
3 | Net Power Exported | kWhr | 139914 | 2918517 | 6890103
4 | Auxiliary power consumption | ( % ) | 11.1657 | 11.5735 | 11.5497
5 | Average Power Generation | MWhr | 6.5625 | 6.2509 | 6.3298
6 | Plant Running Hours | Hrs | 24 | 528 | 1230.66
6 | PLF | ( % ) | 65.625 | 62.5095 | 63.2977
7 | Feed Water consumption | MT | 734 | 15673 | 36772
8 | Boiler Steam Generation | MT | 708 | 15196 | 35690
9 | Bleed steam | MT | 49 | 776 | 1968
10 | Turbine steam consumption | MT | 658 | 13681 | 32358
11 | Condensate Generation | MT | 519 | 11102 | 26283
12 | Auxilairy steam consumption | MT | 18 | 393 | 921
13 | Specific steam consumption | Kg/Kwhr | 4.1778 | 4.1451 | 4.1539
14 | Specific fuel consumption | Kg/Kwhr | 0.86349 | 0.89805 | 0.87717
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2814.5016 | 2792.6354 | 2798.7707
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3878.5836 | 3972.5558 | 3953.1264
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 136 | 2964 | 6833
2 | GCV ( ADB ) | Kcal/kg | 4435
WTP Report
1 | DM water Generation | m3 | 17 | 332 | 822
2 | DM water Consumption | m3 | 15 | 326 | 831
3 | CT Makeup Water Consumption | m3 | 16 | 436 | 974
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1381
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 35 | 395 | 1027
6 | Fly ash to Coal yard(Truck) | nos | 3 | 65 | 131
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 23
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-23 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 151600 | 3452100 | 7941400
2 | Auxiliary power consumption | kWhr | 18383 | 400366 | 918080
3 | Net Power Exported | kWhr | 133217 | 3051734 | 7023320
4 | Auxiliary power consumption | ( % ) | 12.126 | 11.5978 | 11.5607
5 | Average Power Generation | MWhr | 6.3167 | 6.2538 | 6.3295
6 | Plant Running Hours | Hrs | 24 | 552 | 1254.66
6 | PLF | ( % ) | 63.1667 | 62.538 | 63.2952
7 | Feed Water consumption | MT | 723 | 16396 | 37495
8 | Boiler Steam Generation | MT | 690 | 15886 | 36380
9 | Bleed steam | MT | 48 | 824 | 2016
10 | Turbine steam consumption | MT | 637 | 14318 | 32995
11 | Condensate Generation | MT | 508 | 11610 | 26791
12 | Auxilairy steam consumption | MT | 17 | 410 | 938
13 | Specific steam consumption | Kg/Kwhr | 4.2018 | 4.1476 | 4.1548
14 | Specific fuel consumption | Kg/Kwhr | 0.93668 | 0.89974 | 0.87831
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2832.1966 | 2794.3727 | 2799.4088
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3927.0854 | 3970.559 | 3952.6293
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 142 | 3106 | 6975
2 | GCV ( ADB ) | Kcal/kg | 4200
WTP Report
1 | DM water Generation | m3 | 20 | 352 | 842
2 | DM water Consumption | m3 | 22 | 348 | 853
3 | CT Makeup Water Consumption | m3 | 20 | 456 | 994
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1378
5 | Fly ash to cement mill | MT | 40 | 435 | 1067
6 | Fly ash to Coal yard(Truck) | nos | 3 | 68 | 134
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 24
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-24 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 181400 | 3633500 | 8122800
2 | Auxiliary power consumption | kWhr | 17879 | 418245 | 935959
3 | Net Power Exported | kWhr | 163521 | 3215255 | 7186841
4 | Auxiliary power consumption | ( % ) | 9.8561 | 11.5108 | 11.5226
5 | Average Power Generation | MWhr | 7.5583 | 6.3082 | 6.3526
6 | Plant Running Hours | Hrs | 24 | 576 | 1278.66
6 | PLF | ( % ) | 75.5833 | 63.0816 | 63.5259
7 | Feed Water consumption | MT | 825 | 17221 | 38320
8 | Boiler Steam Generation | MT | 802 | 16688 | 37182
9 | Bleed steam | MT | 68 | 892 | 2084
10 | Turbine steam consumption | MT | 757 | 15075 | 33752
11 | Condensate Generation | MT | 588 | 12198 | 27379
12 | Auxilairy steam consumption | MT | 18 | 428 | 956
13 | Specific steam consumption | Kg/Kwhr | 4.1731 | 4.1489 | 4.1552
14 | Specific fuel consumption | Kg/Kwhr | 0.88203 | 0.89886 | 0.87839
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2810.8104 | 2728.2705 | 2731.4421
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3814.675 | 3962.7766 | 3949.5485
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 160 | 3266 | 7135
2 | GCV ( ADB ) | Kcal/kg | 4309
WTP Report
1 | DM water Generation | m3 | 15 | 367 | 857
2 | DM water Consumption | m3 | 14 | 362 | 867
3 | CT Makeup Water Consumption | m3 | 18 | 474 | 1012
4 | Fly ash combustible/ GCV | % / kcal/kg | 17.46 | 1362
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 60 | 495 | 1127
6 | Fly ash to Coal yard(Truck) | nos | 4 | 72 | 138
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 25
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-25 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165000 | 3798500 | 8287800
2 | Auxiliary power consumption | kWhr | 17657 | 435902 | 953616
3 | Net Power Exported | kWhr | 147343 | 3362598 | 7334184
4 | Auxiliary power consumption | ( % ) | 10.7012 | 11.4756 | 11.5063
5 | Average Power Generation | MWhr | 6.875 | 6.3308 | 6.3622
6 | Plant Running Hours | Hrs | 24 | 600 | 1302.66
6 | PLF | ( % ) | 68.75 | 63.3083 | 63.6221
7 | Feed Water consumption | MT | 756 | 17977 | 39076
8 | Boiler Steam Generation | MT | 730 | 17418 | 37912
9 | Bleed steam | MT | 57 | 949 | 2141
10 | Turbine steam consumption | MT | 689 | 15764 | 34441
11 | Condensate Generation | MT | 536 | 12734 | 27915
12 | Auxilairy steam consumption | MT | 18 | 446 | 974
13 | Specific steam consumption | Kg/Kwhr | 4.1758 | 4.1501 | 4.1556
14 | Specific fuel consumption | Kg/Kwhr | 0.87273 | 0.89772 | 0.87828
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.6485 | 2795.9516 | 2799.9219
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.3271 | 3956.4585 | 3946.9161
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 144 | 3410 | 7279
2 | GCV ( ADB ) | Kcal/kg | 4350
WTP Report
1 | DM water Generation | m3 | 12 | 379 | 869
2 | DM water Consumption | m3 | 13 | 375 | 880
3 | CT Makeup Water Consumption | m3 | 18 | 492 | 1030
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1338
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 30 | 525 | 1157
6 | Fly ash to Coalyard(Truck) | nos | 2 | 74 | 140
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 26
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-26 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 143500 | 3942000 | 8431300
2 | Auxiliary power consumption | kWhr | 17264 | 453166 | 970880
3 | Net Power Exported | kWhr | 126236 | 3488834 | 7460420
4 | Auxiliary power consumption | ( % ) | 12.0307 | 11.4958 | 11.5152
5 | Average Power Generation | MWhr | 5.9792 | 6.3173 | 6.3553
6 | Plant Running Hours | Hrs | 24 | 624 | 1326.66
6 | PLF | ( % ) | 59.7917 | 63.1731 | 63.5528
7 | Feed Water consumption | MT | 701 | 18678 | 39777
8 | Boiler Steam Generation | MT | 679 | 18097 | 38591
9 | Bleed steam | MT | 21 | 970 | 2162
10 | Turbine steam consumption | MT | 592 | 16356 | 35033
11 | Condensate Generation | MT | 497 | 13231 | 28412
12 | Auxilairy steam consumption | MT | 18 | 464 | 992
13 | Specific steam consumption | Kg/Kwhr | 4.1254 | 4.1492 | 4.1551
14 | Specific fuel consumption | Kg/Kwhr | 0.9338 | 0.89904 | 0.87922
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2779.9721 | 2795.3699 | 2799.5824
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4082.6141 | 3961.0509 | 3949.2257
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 134 | 3544 | 7413
2 | GCV ( ADB ) | Kcal/kg | 4366
WTP Report
1 | DM water Generation | m3 | 16 | 395 | 885
2 | DM water Consumption | m3 | 17 | 392 | 897
3 | CT Makeup Water Consumption | m3 | 18 | 510 | 1048
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1325
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 550 | 1182
6 | Fly ash to Coalyard(Truck) | nos | 4 | 78 | 144
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 27
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-27 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 167100 | 4109100 | 8598400
2 | Auxiliary power consumption | kWhr | 17580 | 470746 | 988460
3 | Net Power Exported | kWhr | 149520 | 3638354 | 7609940
4 | Auxiliary power consumption | ( % ) | 10.5206 | 11.4562 | 11.4959
5 | Average Power Generation | MWhr | 6.9625 | 6.3412 | 6.3661
6 | Plant Running Hours | Hrs | 24 | 648 | 1350.66
6 | PLF | ( % ) | 69.625 | 63.412 | 63.6607
7 | Feed Water consumption | MT | 758 | 19436 | 40535
8 | Boiler Steam Generation | MT | 740 | 18837 | 39331
9 | Bleed steam | MT | 54 | 1024 | 2216
10 | Turbine steam consumption | MT | 696 | 17052 | 35729
11 | Condensate Generation | MT | 540 | 13771 | 28952
12 | Auxilairy steam consumption | MT | 17 | 481 | 1009
13 | Specific steam consumption | Kg/Kwhr | 4.1652 | 4.1498 | 4.1553
14 | Specific fuel consumption | Kg/Kwhr | 0.8857 | 0.89849 | 0.87935
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.6732 | 2795.7889 | 2799.7008
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3820.9885 | 3955.3552 | 3946.7335
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 148 | 3692 | 7561
2 | GCV ( ADB ) | Kcal/kg | 4288
WTP Report
1 | DM water Generation | m3 | 14 | 409 | 899
2 | DM water Consumption | m3 | 14 | 406 | 911
3 | CT Makeup Water Consumption | m3 | 18 | 528 | 1066
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1387
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 53 | 603 | 1235
6 | Fly ash to Coalyard(Truck) | nos | 1 | 79 | 145
7 | Fly ash to Dumpyard(Truck) | nos |  | 0 | 0

## 28
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-28 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 175300 | 4284400 | 8773700
2 | Auxiliary power consumption | kWhr | 17127 | 487873 | 1005587
3 | Net Power Exported | kWhr | 158173 | 3796527 | 7768113
4 | Auxiliary power consumption | ( % ) | 9.7701 | 11.3872 | 11.4614
5 | Average Power Generation | MWhr | 7.3042 | 6.3756 | 6.3825
6 | Plant Running Hours | Hrs | 24 | 672 | 1374.66
6 | PLF | ( % ) | 73.0417 | 63.756 | 63.8245
7 | Feed Water consumption | MT | 796 | 20232 | 41331
8 | Boiler Steam Generation | MT | 775 | 19612 | 40106
9 | Bleed steam | MT | 59 | 1083 | 2275
10 | Turbine steam consumption | MT | 733 | 17785 | 36462
11 | Condensate Generation | MT | 570 | 14341 | 29522
12 | Auxilairy steam consumption | MT | 18 | 499 | 1027
13 | Specific steam consumption | Kg/Kwhr | 4.1814 | 4.1511 | 4.1558
14 | Specific fuel consumption | Kg/Kwhr | 0.87849 | 0.89768 | 0.87933
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.138 | 2796.6215 | 2800.0292
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3814.5231 | 3949.5929 | 3944.0919
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 154 | 3846 | 7715
2 | GCV ( ADB ) | Kcal/kg | 4299
WTP Report
1 | DM water Generation | m3 | 12 | 421 | 911
2 | DM water Consumption | m3 | 12 | 418 | 923
3 | CT Makeup Water Consumption | m3 | 17 | 545 | 1083
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1451
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 40 | 643 | 1275
6 | Fly ash to Coalyard(Truck) | nos | 3 | 82 | 148
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 29
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-29 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 160900 | 4445300 | 8934600
2 | Auxiliary power consumption | kWhr | 17411 | 505284 | 1022998
3 | Net Power Exported | kWhr | 143489 | 3940016 | 7911602
4 | Auxiliary power consumption | ( % ) | 10.821 | 11.3667 | 11.4498
5 | Average Power Generation | MWhr | 6.7042 | 6.3869 | 6.388
6 | Plant Running Hours | Hrs | 24 | 696 | 1398.66
6 | PLF | ( % ) | 67.0417 | 63.8693 | 63.8797
7 | Feed Water consumption | MT | 742 | 20974 | 42073
8 | Boiler Steam Generation | MT | 715 | 20327 | 40821
9 | Bleed steam | MT | 53 | 1136 | 2328
10 | Turbine steam consumption | MT | 674 | 18459 | 37136
11 | Condensate Generation | MT | 528 | 14869 | 30050
12 | Auxilairy steam consumption | MT | 19 | 518 | 1046
13 | Specific steam consumption | Kg/Kwhr | 4.1889 | 4.1525 | 4.1564
14 | Specific fuel consumption | Kg/Kwhr | 0.88254 | 0.89713 | 0.87939
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2822.138 | 2797.545 | 2800.4273
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3834.162 | 3945.4148 | 3942.1123
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 142 | 3988 | 7857
2 | GCV ( ADB ) | Kcal/kg | 4325
WTP Report
1 | DM water Generation | m3 | 14 | 435 | 925
2 | DM water Consumption | m3 | 16 | 434 | 939
3 | CT Makeup Water Consumption | m3 | 18 | 563 | 1101
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1345
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 35 | 678 | 1310
6 | Fly ash to Coalyard(Truck) | nos | 2 | 84 | 150
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 30
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176700 | 4622000 | 9111300
2 | Auxiliary power consumption | kWhr | 17616 | 522900 | 1040614
3 | Net Power Exported | kWhr | 159084 | 4099100 | 8070686
4 | Auxiliary power consumption | ( % ) | 9.9694 | 11.3133 | 11.4211
5 | Average Power Generation | MWhr | 7.3625 | 6.4194 | 6.4044
6 | Plant Running Hours | Hrs | 24 | 720 | 1422.66
6 | PLF | ( % ) | 73.625 | 64.1944 | 64.0441
7 | Feed Water consumption | MT | 799 | 21773 | 42872
8 | Boiler Steam Generation | MT | 779 | 21106 | 41600
9 | Bleed steam | MT | 59 | 1195 | 2387
10 | Turbine steam consumption | MT | 734 | 19193 | 37870
11 | Condensate Generation | MT | 571 | 15440 | 30621
12 | Auxilairy steam consumption | MT | 17 | 535 | 1063
13 | Specific steam consumption | Kg/Kwhr | 4.1539 | 4.1525 | 4.1564
14 | Specific fuel consumption | Kg/Kwhr | 0.87719 | 0.89637 | 0.87935
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2797.8042 | 2797.555 | 2800.3765
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3803.8324 | 3940.0021 | 3939.4305
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 155 | 4143 | 8012
2 | GCV ( ADB ) | Kcal/kg | 4294
WTP Report
1 | DM water Generation | m3 | 16 | 451 | 941
2 | DM water Consumption | m3 | 13 | 447 | 952
3 | CT Makeup Water Consumption | m3 | 17 | 580 | 1118
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1389
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 703 | 1335
6 | Fly ash to Coalyard(Truck) | nos | 3 | 87 | 153
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 31
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 177800 | 4799800 | 9289100
2 | Auxiliary power consumption | kWhr | 17870 | 540770 | 1058484
3 | Net Power Exported | kWhr | 159930 | 4259030 | 8230616
4 | Auxiliary power consumption | ( % ) | 10.0506 | 11.2665 | 11.3949
5 | Average Power Generation | MWhr | 7.4083 | 6.4513 | 6.4211
6 | Plant Running Hours | Hrs | 24 | 744 | 1446.66
6 | PLF | ( % ) | 74.0833 | 64.5134 | 64.2107
7 | Feed Water consumption | MT | 816 | 22589 | 43688
8 | Boiler Steam Generation | MT | 789 | 21895 | 42389
9 | Bleed steam | MT | 58 | 1253 | 2445
10 | Turbine steam consumption | MT | 744 | 19937 | 38614
11 | Condensate Generation | MT | 585 | 16025 | 31206
12 | Auxilairy steam consumption | MT | 18 | 553 | 1081
13 | Specific steam consumption | Kg/Kwhr | 4.1845 | 4.1537 | 4.1569
14 | Specific fuel consumption | Kg/Kwhr | 0.89989 | 0.8965 | 0.87974
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2818.6839 | 2798.3376 | 2800.7269
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3828.8267 | 3935.8838 | 3937.3135
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 160 | 4303 | 8172
2 | GCV ( ADB ) | Kcal/kg | 4262
WTP Report
1 | DM water Generation | m3 | 14 | 465 | 955
2 | DM water Consumption | m3 | 15 | 462 | 967
3 | CT Makeup Water Consumption | m3 | 18 | 598 | 1136
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.66 | 1366
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 36 | 739 | 1371
6 | Fly ash to Coalyard(Truck) | nos | 2 | 89 | 155
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0