## 0
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-03-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr
2 | Auxiliary power consumption | kWhr
3 | Net Power Exported | kWhr | 0 | 0 | 0
4 | Auxiliary power consumption | ( % ) | 0 | 0 | 0
5 | Average Power Generation | MWhr | 0 | 0 | 0
6 | Plant Running Hours | Hrs | 0 | 0 | 0
6 | PLF | ( % ) | 0 | 0 | 0
7 | Feed Water consumption | MT
8 | Boiler Steam Generation | MT
9 | Bleed steam | MT
10 | Turbine steam consumption | MT
11 | Condensate Generation | MT
12 | Auxilairy steam consumption | MT
13 | Specific steam consumption | Kg/Kwhr | 0 | 0 | 0
14 | Specific fuel consumption | Kg/Kwhr | 0 | 0 | 0
15 | Heat Rate(TG)2880 | Kcal/Kwh | 0 | 0 | 0
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 0 | 0 | 0
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 0 | 0 | 0
2 | GCV ( ADB ) | Kcal/kg | 0
WTP Report
1 | DM water Generation | m3
2 | DM water Consumption | m3
3 | CT Makeup Water Consumption | m3
4 | Fly ash combustible/ GCV | % / kcal/kg
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT
6 | Fly ash to Coalyard(Truck) | nos
7 | Fly ash to Dumpyard(Truck) | nos

## 1
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-01 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 29100 | 29100 | 29100
2 | Auxiliary power consumption | kWhr | 6960 | 6960 | 6960
3 | Net Power Exported | kWhr | 22140 | 22140 | 22140
4 | Auxiliary power consumption | ( % ) | 23.9175 | 23.9175 | 23.9175
5 | Average Power Generation | MWhr | 4.3694 | 4.3694 | 4.3694
6 | Plant Running Hours | Hrs | 6.66 | 6.66 | 6.66
6 | PLF | ( % ) | 43.6937 | 43.6937 | 43.6937
7 | Feed Water consumption | MT | 177 | 177 | 177
8 | Boiler Steam Generation | MT | 157 | 157 | 157
9 | Bleed steam | MT | 0 | 0 | 0
10 | Turbine steam consumption | MT | 124 | 124 | 124
11 | Condensate Generation | MT | 119 | 119 | 119
12 | Auxilairy steam consumption | MT | 5 | 5 | 5
13 | Specific steam consumption | Kg/Kwhr | 4.2612 | 4.2612 | 4.2612
14 | Specific fuel consumption | Kg/Kwhr | 0.75601 | 0.75601 | 0.75601
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2938.9003 | 2938.9003 | 2938.9003
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4655.0797 | 4655.0797 | 4655.0797
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 22 | 22 | 22
2 | GCV ( ADB ) | Kcal/kg | 4929
WTP Report
1 | DM water Generation | m2 | 47 | 47 | 47
2 | DM water Consumption | m3 | 69 | 69 | 69
3 | CT Makeup Water Consumption | m3 | 28 | 28 | 28
4 | Fly ash combustible/ GCV | % / kcal/kg | 26 | 1557
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 6 | 6 | 6
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 0
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 2
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-02 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 159500 | 188600 | 188600
2 | Auxiliary power consumption | kWhr | 17514 | 24474 | 24474
3 | Net Power Exported | kWhr | 141986 | 164126 | 164126
4 | Auxiliary power consumption | ( % ) | 10.9806 | 12.9767 | 12.9767
5 | Average Power Generation | MWhr | 6.6458 | 6.1513 | 6.1513
6 | Plant Running Hours | Hrs | 24 | 30.66 | 30.66
7 | PLF | ( % ) | 66.4583 | 61.5134 | 61.5134
8 | Feed Water consumption | MT | 757 | 934 | 934
9 | Boiler Steam Generation | MT | 740 | 897 | 897
10 | Bleed steam | MT | 14 | 14 | 14
11 | Turbine steam consumption | MT | 666 | 790 | 790
12 | Condensate Generation | MT | 565 | 684 | 684
13 | Auxilairy steam consumption | MT | 18 | 23 | 23
14 | Specific steam consumption | Kg/Kwhr | 4.1755 | 4.1888 | 4.1888
15 | Specific fuel consumption | Kg/Kwhr | 0.8652 | 0.84836 | 0.84836
16 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.4013 | 2831.9194 | 2831.9194
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4003.0544 | 4103.6585 | 4103.6585
18 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 160 | 160
2 | GCV ( ADB ) | Kcal/kg | 4607
WTP Report
1 | DM water Generation | m3 | 18 | 65 | 65
2 | DM water Consumption | m3 | 12 | 81 | 81
3 | CT Makeup Water Consumption | m3 | 18 | 46 | 46
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1422
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 53 | 53
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 0
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 3
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-03 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 146400 | 335000 | 335000
2 | Auxiliary power consumption | kWhr | 17481 | 41955 | 41955
3 | Net Power Exported | kWhr | 128919 | 293045 | 293045
4 | Auxiliary power consumption | ( % ) | 11.9406 | 12.5239 | 12.5239
5 | Average Power Generation | MWhr | 6.1 | 6.1288 | 6.1288
6 | Plant Running Hours | Hrs | 24 | 54.66 | 54.66
6 | PLF | ( % ) | 61 | 61.288 | 61.288
7 | Feed Water consumption | MT | 693 | 1627 | 1627
8 | Boiler Steam Generation | MT | 678 | 1575 | 1575
9 | Bleed steam | MT | 21 | 35 | 35
10 | Turbine steam consumption | MT | 619 | 1409 | 1409
11 | Condensate Generation | MT | 518 | 1202 | 1202
12 | Auxilairy steam consumption | MT | 18 | 41 | 41
13 | Specific steam consumption | Kg/Kwhr | 4.2281 | 4.206 | 4.206
14 | Specific fuel consumption | Kg/Kwhr | 0.86066 | 0.85373 | 0.85373
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2848.6134 | 2839.2149 | 2839.2149
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3995.8491 | 4056.5442 | 4056.5442
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 126 | 286 | 286
2 | GCV ( ADB ) | Kcal/kg | 4636
WTP Report
1 | DM water Generation | m3 | 12 | 77 | 77
2 | DM water Consumption | m3 | 15 | 96 | 96
3 | CT Makeup Water Consumption | m3 | 20 | 66 | 66
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.4 | 1417
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 43 | 96 | 96
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 0
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 4
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-04 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 130100 | 465100 | 465100
2 | Auxiliary power consumption | kWhr | 17368 | 59323 | 59323
3 | Net Power Exported | kWhr | 112732 | 405777 | 405777
4 | Auxiliary power consumption | ( % ) | 13.3497 | 12.7549 | 12.7549
5 | Average Power Generation | MWhr | 5.4208 | 5.9128 | 5.9128
6 | Plant Running Hours | Hrs | 24 | 78.66 | 78.66
6 | PLF | ( % ) | 54.2083 | 59.1279 | 59.1279
7 | Feed Water consumption | MT | 647 | 2274 | 2274
8 | Boiler Steam Generation | MT | 628 | 2203 | 2203
9 | Bleed steam | MT | 44 | 79 | 79
10 | Turbine steam consumption | MT | 567 | 1976 | 1976
11 | Condensate Generation | MT | 454 | 1656 | 1656
12 | Auxilairy steam consumption | MT | 18 | 59 | 59
13 | Specific steam consumption | Kg/Kwhr | 4.3582 | 4.2485 | 4.2485
14 | Specific fuel consumption | Kg/Kwhr | 0.74558 | 0.82348 | 0.82348
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2936.7487 | 2866.4975 | 2866.4975
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4164.883 | 4086.8493 | 4086.8493
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 97 | 383 | 383
2 | GCV ( ADB ) | Kcal/kg | 4729
WTP Report
1 | DM water Generation | m3 | 17 | 94 | 94
2 | DM water Consumption | m3 | 16 | 112 | 112
3 | CT Makeup Water Consumption | m3 | 18 | 84 | 84
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.89 | 1383
5 | Fly ash to cement mill | MT | 31 | 127 | 127
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 0
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 5
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-05 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 98800 | 563900 | 563900
2 | Auxiliary power consumption | kWhr | 16573 | 75896 | 75896
3 | Net Power Exported | kWhr | 82227 | 488004 | 488004
4 | Auxiliary power consumption | ( % ) | 16.7743 | 13.4591 | 13.4591
5 | Average Power Generation | MWhr | 4.1167 | 5.4929 | 5.4929
6 | Plant Running Hours | Hrs | 24 | 102.66 | 102.66
6 | PLF | ( % ) | 41.1667 | 54.9289 | 54.9289
7 | Feed Water consumption | MT | 529 | 2803 | 2803
8 | Boiler Steam Generation | MT | 521 | 2724 | 2724
9 | Bleed steam | MT | 24 | 103 | 103
10 | Turbine steam consumption | MT | 453 | 2429 | 2429
11 | Condensate Generation | MT | 365 | 2021 | 2021
12 | Auxilairy steam consumption | MT | 18 | 77 | 77
13 | Specific steam consumption | Kg/Kwhr | 4.585 | 4.3075 | 4.3075
14 | Specific fuel consumption | Kg/Kwhr | 0.92105 | 0.84057 | 0.84057
15 | Heat Rate(TG)2880 | Kcal/Kwh | 3089.666 | 2905.5985 | 2905.5985
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4549.8936 | 4167.9785 | 4167.9785
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 91 | 474 | 474
2 | GCV ( ADB ) | Kcal/kg | 4579
WTP Report
1 | DM water Generation | m3 | 12 | 106 | 106
2 | DM water Consumption | m3 | 13 | 125 | 125
3 | CT Makeup Water Consumption | m3 | 18 | 102 | 102
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1380
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 15 | 142 | 142
6 | Fly ash to Coal yard(Truck) | nos | 2 | 2 | 2
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 6
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-06 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 142900 | 706800 | 706800
2 | Auxiliary power consumption | kWhr | 17594 | 93490 | 93490
3 | Net Power Exported | kWhr | 125306 | 613310 | 613310
4 | Auxiliary power consumption | ( % ) | 12.3121 | 13.2272 | 13.2272
5 | Average Power Generation | MWhr | 5.9542 | 5.5803 | 5.5803
6 | Plant Running Hours | Hrs | 24 | 126.66 | 126.66
6 | PLF | ( % ) | 59.5417 | 55.8029 | 55.8029
7 | Feed Water consumption | MT | 665 | 3468 | 3468
8 | Boiler Steam Generation | MT | 655 | 3379 | 3379
9 | Bleed steam | MT | 34 | 137 | 137
10 | Turbine steam consumption | MT | 613 | 3042 | 3042
11 | Condensate Generation | MT | 506 | 2527 | 2527
12 | Auxilairy steam consumption | MT | 19 | 96 | 96
13 | Specific steam consumption | Kg/Kwhr | 4.2897 | 4.3039 | 4.3039
14 | Specific fuel consumption | Kg/Kwhr | 0.85374 | 0.84324 | 0.84324
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2889.2862 | 2902.3005 | 2902.3005
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3954.8456 | 4124.8875 | 4124.8875
17 | DG Power Generation | kWhr |  | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 122 | 596 | 596
2 | GCV ( ADB ) | Kcal/kg | 4639
WTP Report
1 | DM water Generation | m3 | 10 | 116 | 116
2 | DM water Consumption | m3 | 11 | 136 | 136
3 | CT Makeup Water Consumption | m3 | 19 | 121 | 121
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1326
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 19 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 2 | 4 | 4
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 7
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-07 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 169500 | 876300 | 876300
2 | Auxiliary power consumption | kWhr | 18050 | 111540 | 111540
3 | Net Power Exported | kWhr | 151450 | 764760 | 764760
4 | Auxiliary power consumption | ( % ) | 10.649 | 12.7285 | 12.7285
5 | Average Power Generation | MWhr | 7.0625 | 5.8164 | 5.8164
6 | Plant Running Hours | Hrs | 24 | 150.66 | 150.66
6 | PLF | ( % ) | 70.625 | 58.1641 | 58.1641
7 | Feed Water consumption | MT | 772 | 4240 | 4240
8 | Boiler Steam Generation | MT | 760 | 4139 | 4139
9 | Bleed steam | MT | 55 | 192 | 192
10 | Turbine steam consumption | MT | 716 | 3758 | 3758
11 | Condensate Generation | MT | 568 | 3095 | 3095
12 | Auxilairy steam consumption | MT | 18 | 114 | 114
13 | Specific steam consumption | Kg/Kwhr | 4.2242 | 4.2885 | 4.2885
14 | Specific fuel consumption | Kg/Kwhr | 0.83776 | 0.84218 | 0.84218
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2845.0029 | 2891.2176 | 2891.2176
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3868.6937 | 4075.3328 | 4075.3328
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 142 | 738 | 738
2 | GCV ( ADB ) | Kcal/kg | 4594
1 | DM water Generation | m3 | 15 | 131 | 131
2 | DM water Consumption | m3 | 12 | 148 | 148
3 | CT Makeup Water Consumption | m3 | 18 | 139 | 139
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1422
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 5 | 9 | 9
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 8
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-08 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 174900 | 1051200 | 1051200
2 | Auxiliary power consumption | kWhr | 18185 | 129725 | 129725
3 | Net Power Exported | kWhr | 156715 | 921475 | 921475
4 | Auxiliary power consumption | ( % ) | 10.3974 | 12.3407 | 12.3407
5 | Average Power Generation | MWhr | 7.2875 | 6.0186 | 6.0186
6 | Plant Running Hours | Hrs | 24 | 174.66 | 174.66
6 | PLF | ( % ) | 72.875 | 60.1855 | 60.1855
7 | Feed Water consumption | MT | 800 | 5040 | 5040
8 | Boiler Steam Generation | MT | 775 | 4914 | 4914
9 | Bleed steam | MT | 61 | 253 | 253
10 | Turbine steam consumption | MT | 729 | 4487 | 4487
11 | Condensate Generation | MT | 647 | 3742 | 3742
12 | Auxilairy steam consumption | MT | 18 | 132 | 132
13 | Specific steam consumption | Kg/Kwhr | 4.1681 | 4.2685 | 4.2685
14 | Specific fuel consumption | Kg/Kwhr | 0.85192 | 0.8438 | 0.8438
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2807.7015 | 2877.3221 | 2877.3221
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3823.247 | 4033.3904 | 4033.3904
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 149 | 887 | 887
2 | GCV ( ADB ) | Kcal/kg | 4480
WTP Report
1 | DM water Generation | m3 | 15 | 146 | 146
2 | DM water Consumption | m3 | 15 | 163 | 163
3 | CT Makeup Water Consumption | m3 | 15 | 154 | 154
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1358
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 4 | 13 | 13
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 9
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-09 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 154800 | 1206000 | 1206000
2 | Auxiliary power consumption | kWhr | 17768 | 147493 | 147493
3 | Net Power Exported | kWhr | 137032 | 1058507 | 1058507
4 | Auxiliary power consumption | ( % ) | 11.478 | 12.2299 | 12.2299
5 | Average Power Generation | MWhr | 6.45 | 6.0707 | 6.0707
6 | Plant Running Hours | Hrs | 24 | 198.66 | 198.66
6 | PLF | ( % ) | 64.5 | 60.7067 | 60.7067
7 | Feed Water consumption | MT | 728 | 5768 | 5768
8 | Boiler Steam Generation | MT | 704 | 5618 | 5618
9 | Bleed steam | MT | 49 | 302 | 302
10 | Turbine steam consumption | MT | 647 | 5134 | 5134
11 | Condensate Generation | MT | 519 | 4261 | 4261
12 | Auxilairy steam consumption | MT | 18 | 150 | 150
13 | Specific steam consumption | Kg/Kwhr | 4.1796 | 4.257 | 4.257
14 | Specific fuel consumption | Kg/Kwhr | 0.88501 | 0.84909 | 0.84909
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.3501 | 2869.4959 | 2869.4959
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3923.9382 | 4019.3413 | 4019.3413
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 137 | 1024 | 1024
2 | GCV ( ADB ) | Kcal/kg | 4424
WTP Report
1 | DM water Generation | m3 | 20 | 166 | 166
2 | DM water Consumption | m3 | 18 | 181 | 181
3 | CT Makeup Water Consumption | m3 | 17 | 171 | 171
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1406
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 5 | 18 | 18
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 10
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-10 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 168800 | 1374800 | 1374800
2 | Auxiliary power consumption | kWhr | 18129 | 165622 | 165622
3 | Net Power Exported | kWhr | 150671 | 1209178 | 1209178
4 | Auxiliary power consumption | ( % ) | 10.7399 | 12.047 | 12.047
5 | Average Power Generation | MWhr | 7.0333 | 6.1744 | 6.1744
6 | Plant Running Hours | Hrs | 24 | 222.66 | 222.66
6 | PLF | ( % ) | 70.3333 | 61.7444 | 61.7444
7 | Feed Water consumption | MT | 797 | 6565 | 6565
8 | Boiler Steam Generation | MT | 760 | 6378 | 6378
9 | Bleed steam | MT | 32 | 334 | 334
10 | Turbine steam consumption | MT | 689 | 5823 | 5823
11 | Condensate Generation | MT | 577 | 4838 | 4838
12 | Auxilairy steam consumption | MT | 18 | 168 | 168
13 | Specific steam consumption | Kg/Kwhr | 4.0818 | 4.2355 | 4.2355
14 | Specific fuel consumption | Kg/Kwhr | 0.84716 | 0.84885 | 0.84885
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2750.3969 | 2854.8727 | 2854.8727
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3884.7369 | 4002.8144 | 4002.8144
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 143 | 1167 | 1167
2 | GCV ( ADB ) | Kcal/kg | 4580
WTP Report
1 | DM water Generation | m3 | 17 | 183 | 183
2 | DM water Consumption | m3 | 19 | 200 | 200
3 | CT Makeup Water Consumption | m3 | 16 | 187 | 187
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1374
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 4 | 22 | 22
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 11
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-11 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 159600 | 1534400 | 1534400
2 | Auxiliary power consumption | kWhr | 17846 | 183468 | 183468
3 | Net Power Exported | kWhr | 141754 | 1350932 | 1350932
4 | Auxiliary power consumption | ( % ) | 11.1817 | 11.957 | 11.957
5 | Average Power Generation | MWhr | 6.65 | 6.2207 | 6.2207
6 | Plant Running Hours | Hrs | 24 | 246.66 | 246.66
6 | PLF | ( % ) | 66.5 | 62.2071 | 62.2071
7 | Feed Water consumption | MT | 747 | 7312 | 7312
8 | Boiler Steam Generation | MT | 720 | 7098 | 7098
9 | Bleed steam | MT | 53 | 387 | 387
10 | Turbine steam consumption | MT | 660 | 6483 | 6483
11 | Condensate Generation | MT | 531 | 5369 | 5369
12 | Auxilairy steam consumption | MT | 18 | 186 | 186
13 | Specific steam consumption | Kg/Kwhr | 4.1353 | 4.2251 | 4.2251
14 | Specific fuel consumption | Kg/Kwhr | 0.87093 | 0.85115 | 0.85115
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2786.8421 | 2847.7965 | 2847.7965
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3892.4234 | 3991.3321 | 3991.3321
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 139 | 1306 | 1306
2 | GCV ( ADB ) | Kcal/kg | 4442
WTP Report
1 | DM water Generation | m3 | 20 | 203 | 203
2 | DM water Consumption | m3 | 20 | 220 | 220
3 | CT Makeup Water Consumption | m3 | 18 | 205 | 205
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1385
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 161 | 161
6 | Fly ash to Coal yard(Truck) | nos | 4 | 26 | 26
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 12
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-12 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 168000 | 1702400 | 1702400
2 | Auxiliary power consumption | kWhr | 17958 | 201426 | 201426
3 | Net Power Exported | kWhr | 150042 | 1500974 | 1500974
4 | Auxiliary power consumption | ( % ) | 10.6893 | 11.8319 | 11.8319
5 | Average Power Generation | MWhr | 7 | 6.2898 | 6.2898
6 | Plant Running Hours | Hrs | 24 | 270.66 | 270.66
6 | PLF | ( % ) | 70 | 62.8981 | 62.8981
7 | Feed Water consumption | MT | 764 | 8076 | 8076
8 | Boiler Steam Generation | MT | 751 | 7849 | 7849
9 | Bleed steam | MT | 53 | 440 | 440
10 | Turbine steam consumption | MT | 696 | 7179 | 7179
11 | Condensate Generation | MT | 548 | 5917 | 5917
12 | Auxilairy steam consumption | MT | 18 | 204 | 204
13 | Specific steam consumption | Kg/Kwhr | 4.1429 | 4.217 | 4.217
14 | Specific fuel consumption | Kg/Kwhr | 0.88095 | 0.85409 | 0.85409
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2790.6429 | 2842.1564 | 2842.1564
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3857.0131 | 3978.077 | 3978.077
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 148 | 1454 | 1454
2 | GCV ( ADB ) | Kcal/kg | 4380
WTP Report
1 | DM water Generation | m3 | 15 | 218 | 218
2 | DM water Consumption | m3 | 14 | 234 | 234
3 | CT Makeup Water Consumption | m3 | 18 | 223 | 223
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1347
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 186 | 186
6 | Fly ash to Coal yard(Truck) | nos | 3 | 29 | 29
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 13
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-13 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 172100 | 1874500 | 1874500
2 | Auxiliary power consumption | kWhr | 18115 | 219541 | 219541
3 | Net Power Exported | kWhr | 153985 | 1654959 | 1654959
4 | Auxiliary power consumption | ( % ) | 10.5259 | 11.712 | 11.712
5 | Average Power Generation | MWhr | 7.1708 | 6.3616 | 6.3616
6 | Plant Running Hours | Hrs | 24 | 294.66 | 294.66
6 | PLF | ( % ) | 71.7083 | 63.6157 | 63.6157
7 | Feed Water consumption | MT | 781 | 8857 | 8857
8 | Boiler Steam Generation | MT | 767 | 8616 | 8616
9 | Bleed steam | MT | 55 | 495 | 495
10 | Turbine steam consumption | MT | 712 | 7891 | 7891
11 | Condensate Generation | MT | 560 | 6477 | 6477
12 | Auxilairy steam consumption | MT | 18 | 222 | 222
13 | Specific steam consumption | Kg/Kwhr | 4.1371 | 4.2097 | 4.2097
14 | Specific fuel consumption | Kg/Kwhr | 0.85997 | 0.85463 | 0.85463
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2786.5543 | 2837.0515 | 2837.0515
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3845.3419 | 3965.8904 | 3965.8904
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 148 | 1602 | 1602
2 | GCV ( ADB ) | Kcal/kg | 4473
WTP Report
1 | DM water Generation | m3 | 14 | 232 | 232
2 | DM water Consumption | m3 | 13 | 247 | 247
3 | CT Makeup Water Consumption | m3 | 18 | 241 | 241
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1375
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 30 | 216 | 216
6 | Fly ash to Coal yard(Truck) | nos | 2 | 31 | 31
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 14
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-14 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 167500 | 2042000 | 2042000
2 | Auxiliary power consumption | kWhr | 18054 | 237595 | 237595
3 | Net Power Exported | kWhr | 149446 | 1804405 | 1804405
4 | Auxiliary power consumption | ( % ) | 10.7785 | 11.6354 | 11.6354
5 | Average Power Generation | MWhr | 6.9792 | 6.4081 | 6.4081
6 | Plant Running Hours | Hrs | 24 | 318.66 | 318.66
6 | PLF | ( % ) | 69.7917 | 64.0808 | 64.0808
7 | Feed Water consumption | MT | 770 | 9627 | 9627
8 | Boiler Steam Generation | MT | 750 | 9366 | 9366
9 | Bleed steam | MT | 51 | 546 | 546
10 | Turbine steam consumption | MT | 700 | 8591 | 8591
11 | Condensate Generation | MT | 555 | 7032 | 7032
12 | Auxilairy steam consumption | MT | 18 | 240 | 240
13 | Specific steam consumption | Kg/Kwhr | 4.1791 | 4.2071 | 4.2071
14 | Specific fuel consumption | Kg/Kwhr | 0.94328 | 0.8619 | 0.8619
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2815.2239 | 2835.261 | 2835.261
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3863.3754 | 3957.4814 | 3957.4814
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 158 | 1760 | 1760
2 | GCV ( ADB ) | Kcal/kg | 4088
WTP Report
1 | DM water Generation | m3 | 16 | 248 | 248
2 | DM water Consumption | m3 | 15 | 262 | 262
3 | CT Makeup Water Consumption | m3 | 18 | 259 | 259
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.51 | 1355
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 216 | 216
6 | Fly ash to Coal yard(Truck) | nos | 4 | 35 | 35
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 15
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-15 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165300 | 2207300 | 2207300
2 | Auxiliary power consumption | kWhr | 18224 | 255819 | 255819
3 | Net Power Exported | kWhr | 147076 | 1951481 | 1951481
4 | Auxiliary power consumption | ( % ) | 11.0248 | 11.5897 | 11.5897
5 | Average Power Generation | MWhr | 6.8875 | 6.4417 | 6.4417
6 | Plant Running Hours | Hrs | 24 | 342.66 | 342.66
6 | PLF | ( % ) | 68.875 | 64.4166 | 64.4166
7 | Feed Water consumption | MT | 756 | 10383 | 10383
8 | Boiler Steam Generation | MT | 738 | 10104 | 10104
9 | Bleed steam | MT | 51 | 597 | 597
10 | Turbine steam consumption | MT | 683 | 9274 | 9274
11 | Condensate Generation | MT | 543 | 7575 | 7575
12 | Auxilairy steam consumption | MT | 18 | 258 | 258
13 | Specific steam consumption | Kg/Kwhr | 4.1319 | 4.2015 | 4.2015
14 | Specific fuel consumption | Kg/Kwhr | 0.87114 | 0.86259 | 0.86259
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2783.66 | 2831.3967 | 2831.3967
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3852.1569 | 3949.5938 | 3949.5938
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 144 | 1904 | 1904
2 | GCV ( ADB ) | Kcal/kg | 4392
WTP Report
1 | DM water Generation | m3 | 16 | 264 | 264
2 | DM water Consumption | m3 | 16 | 278 | 278
3 | CT Makeup Water Consumption | m3 | 17 | 276 | 276
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1388
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 50 | 266 | 266
6 | Fly ash to Coal yard(Truck) | nos | 2 | 37 | 37
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 16
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-16 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 157000 | 2364300 | 2364300
2 | Auxiliary power consumption | kWhr | 17705 | 273524 | 273524
3 | Net Power Exported | kWhr | 139295 | 2090776 | 2090776
4 | Auxiliary power consumption | ( % ) | 11.2771 | 11.5689 | 11.5689
5 | Average Power Generation | MWhr | 6.5417 | 6.4482 | 6.4482
6 | Plant Running Hours | Hrs | 24 | 366.66 | 366.66
6 | PLF | ( % ) | 65.4167 | 64.4821 | 64.4821
7 | Feed Water consumption | MT | 729 | 11112 | 11112
8 | Boiler Steam Generation | MT | 707 | 10811 | 10811
9 | Bleed steam | MT | 40 | 637 | 637
10 | Turbine steam consumption | MT | 647 | 9921 | 9921
11 | Condensate Generation | MT | 520 | 8095 | 8095
12 | Auxilairy steam consumption | MT | 18 | 276 | 276
13 | Specific steam consumption | Kg/Kwhr | 4.121 | 4.1962 | 4.1962
14 | Specific fuel consumption | Kg/Kwhr | 0.91083 | 0.8658 | 0.8658
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2775.9299 | 2827.7135 | 2827.7135
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3885.4401 | 3945.3337 | 3945.3337
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 143 | 2047 | 2047
2 | GCV ( ADB ) | Kcal/kg | 4247
WTP Report
1 | DM water Generation | m3 | 11 | 275 | 275
2 | DM water Consumption | m3 | 13 | 291 | 291
3 | CT Makeup Water Consumption | m3 | 17 | 293 | 293
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1339
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 53 | 319 | 319
6 | Fly ash to Coal yard(Truck) | nos | 0 | 37 | 37
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 17
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-17 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 159000 | 2523300 | 2523300
2 | Auxiliary power consumption | kWhr | 17518 | 291042 | 291042
3 | Net Power Exported | kWhr | 141482 | 2232258 | 2232258
4 | Auxiliary power consumption | ( % ) | 11.0176 | 11.5342 | 11.5342
5 | Average Power Generation | MWhr | 6.625 | 6.4591 | 6.4591
6 | Plant Running Hours | Hrs | 24 | 390.66 | 390.66
6 | PLF | ( % ) | 66.25 | 64.5907 | 64.5907
7 | Feed Water consumption | MT | 728 | 11840 | 11840
8 | Boiler Steam Generation | MT | 714 | 11525 | 11525
9 | Bleed steam | MT | 53 | 690 | 690
10 | Turbine steam consumption | MT | 658 | 10579 | 10579
11 | Condensate Generation | MT | 517 | 8612 | 8612
12 | Auxilairy steam consumption | MT | 19 | 295 | 295
13 | Specific steam consumption | Kg/Kwhr | 4.1384 | 4.1925 | 4.1925
14 | Specific fuel consumption | Kg/Kwhr | 0.93082 | 0.86989 | 0.86989
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2787.9497 | 2825.2079 | 2825.2079
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3874.5525 | 3940.8736 | 3940.8736
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 148 | 2195 | 2195
2 | GCV ( ADB ) | Kcal/kg | 4149
WTP Report
1 | DM water Generation | m3 | 14 | 289 | 289
2 | DM water Consumption | m3 | 15 | 306 | 306
3 | CT Makeup Water Consumption | m3 | 18 | 311 | 311
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1287
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 319 | 319
6 | Fly ash to Coal yard(Truck) | nos | 3 | 40 | 40
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 18
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-18 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 149900 | 2673200 | 2673200
2 | Auxiliary power consumption | kWhr | 17377 | 308419 | 308419
3 | Net Power Exported | kWhr | 132523 | 2364781 | 2364781
4 | Auxiliary power consumption | ( % ) | 11.5924 | 11.5374 | 11.5374
5 | Average Power Generation | MWhr | 6.2458 | 6.4467 | 6.4467
6 | Plant Running Hours | Hrs | 24 | 414.66 | 414.66
6 | PLF | ( % ) | 62.4583 | 64.4673 | 64.4673
7 | Feed Water consumption | MT | 692 | 12532 | 12532
8 | Boiler Steam Generation | MT | 677 | 12202 | 12202
9 | Bleed steam | MT | 52 | 742 | 742
10 | Turbine steam consumption | MT | 619 | 11198 | 11198
11 | Condensate Generation | MT | 486 | 9098 | 9098
12 | Auxilairy steam consumption | MT | 17 | 312 | 312
13 | Specific steam consumption | Kg/Kwhr | 4.1294 | 4.189 | 4.189
14 | Specific fuel consumption | Kg/Kwhr | 0.91394 | 0.87236 | 0.87236
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2782.3015 | 2822.8019 | 2822.8019
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3896.7944 | 3938.4019 | 3938.4019
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 137 | 2332 | 2332
2 | GCV ( ADB ) | Kcal/kg | 4245
WTP Report
1 | DM water Generation | m3 | 17 | 306 | 306
2 | DM water Consumption | m3 | 16 | 322 | 322
3 | CT Makeup Water Consumption | m3 | 18 | 329 | 329
4 | Fly ash combustible/ GCV | % / kcal/kg | 16 | 1304
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 319 | 319
6 | Fly ash to Coal yard(Truck) | nos | 4 | 44 | 44
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 19
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-19 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 140500 | 2813700 | 2813700
2 | Auxiliary power consumption | kWhr | 17323 | 325742 | 325742
3 | Net Power Exported | kWhr | 123177 | 2487958 | 2487958
4 | Auxiliary power consumption | ( % ) | 12.3295 | 11.577 | 11.577
5 | Average Power Generation | MWhr | 5.8542 | 6.4143 | 6.4143
6 | Plant Running Hours | Hrs | 24 | 438.66 | 438.66
6 | PLF | ( % ) | 58.5417 | 64.1431 | 64.1431
7 | Feed Water consumption | MT | 670 | 13202 | 13202
8 | Boiler Steam Generation | MT | 647 | 12849 | 12849
9 | Bleed steam | MT | 34 | 776 | 776
10 | Turbine steam consumption | MT | 579 | 11777 | 11777
11 | Condensate Generation | MT | 472 | 9570 | 9570
12 | Auxilairy steam consumption | MT | 18 | 330 | 330
13 | Specific steam consumption | Kg/Kwhr | 4.121 | 4.1856 | 4.1856
14 | Specific fuel consumption | Kg/Kwhr | 0.9395 | 0.87572 | 0.87572
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2777.274 | 2820.5285 | 2820.5285
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3973.2731 | 3940.1431 | 3940.1431
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 132 | 2464 | 2464
2 | GCV ( ADB ) | Kcal/kg | 4239
WTP Report
1 | DM water Generation | m3 | 19 | 325 | 325
2 | DM water Consumption | m3 | 18 | 340 | 340
3 | CT Makeup Water Consumption | m3 | 18 | 347 | 347
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1258
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 45 | 364 | 364
6 | Fly ash to Coal yard(Truck) | nos | 0 | 44 | 44
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 20
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-20 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 132100 | 2945800 | 2945800
2 | Auxiliary power consumption | kWhr | 17135 | 342877 | 342877
3 | Net Power Exported | kWhr | 114965 | 2602923 | 2602923
4 | Auxiliary power consumption | ( % ) | 12.9712 | 11.6395 | 11.6395
5 | Average Power Generation | MWhr | 5.5042 | 6.3671 | 6.3671
6 | Plant Running Hours | Hrs | 24 | 462.66 | 462.66
6 | PLF | ( % ) | 55.0417 | 63.6709 | 63.6709
7 | Feed Water consumption | MT | 650 | 13852 | 13852
8 | Boiler Steam Generation | MT | 629 | 13478 | 13478
9 | Bleed steam | MT | 22 | 798 | 798
10 | Turbine steam consumption | MT | 543 | 12320 | 12320
11 | Condensate Generation | MT | 456 | 10026 | 10026
12 | Auxilairy steam consumption | MT | 18 | 348 | 348
13 | Specific steam consumption | Kg/Kwhr | 4.1105 | 4.1822 | 4.1822
14 | Specific fuel consumption | Kg/Kwhr | 0.9841 | 0.88058 | 0.88058
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2770.0151 | 2818.2633 | 2818.2633
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4108.3581 | 3947.6865 | 3947.6865
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 130 | 2594 | 2594
2 | GCV ( ADB ) | Kcal/kg | 4164 | 0
WTP Report
1 | DM water Generation | m3 | 17 | 342 | 342
2 | DM water Consumption | m3 | 16 | 356 | 356
3 | CT Makeup Water Consumption | m3 | 18 | 365 | 365
4 | Fly ash combustible/ GCV | % / kcal/kg | 16 | 1289
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 48 | 412 | 412
6 | Fly ash to Coal yard(Truck) | nos | 0 | 44 | 44
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 21
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-21 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 139400 | 3085200 | 3085200
2 | Auxiliary power consumption | kWhr | 17157 | 360034 | 360034
3 | Net Power Exported | kWhr | 122243 | 2725166 | 2725166
4 | Auxiliary power consumption | ( % ) | 12.3077 | 11.6697 | 11.6697
5 | Average Power Generation | MWhr | 5.8083 | 6.3395 | 6.3395
6 | Plant Running Hours | Hrs | 24 | 486.66 | 486.66
6 | PLF | ( % ) | 58.0833 | 63.3954 | 63.3954
7 | Feed Water consumption | MT | 660 | 14512 | 14512
8 | Boiler Steam Generation | MT | 644 | 14122 | 14122
9 | Bleed steam | MT | 41 | 839 | 839
10 | Turbine steam consumption | MT | 579 | 12899 | 12899
11 | Condensate Generation | MT | 464 | 10490 | 10490
12 | Auxilairy steam consumption | MT | 19 | 367 | 367
13 | Specific steam consumption | Kg/Kwhr | 4.1535 | 4.1809 | 4.1809
14 | Specific fuel consumption | Kg/Kwhr | 0.94692 | 0.88357 | 0.88357
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2798.5438 | 2817.3723 | 2817.3723
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3986.0575 | 3949.4202 | 3949.4202
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 132 | 2726 | 2726
2 | GCV ( ADB ) | Kcal/kg | 4179
1 | DM water Generation | m3 | 14 | 356 | 356
2 | DM water Consumption | m3 | 15 | 371 | 371
3 | CT Makeup Water Consumption | m3 | 18 | 383 | 383
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1286
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 18 | 430 | 430
6 | Fly ash to Coal yard(Truck) | nos | 3 | 47 | 47
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 22
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-22 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 148800 | 3234000 | 3234000
2 | Auxiliary power consumption | kWhr | 17638 | 377672 | 377672
3 | Net Power Exported | kWhr | 131162 | 2856328 | 2856328
4 | Auxiliary power consumption | ( % ) | 11.8535 | 11.6782 | 11.6782
5 | Average Power Generation | MWhr | 6.2 | 6.333 | 6.333
6 | Plant Running Hours | Hrs | 24 | 510.66 | 510.66
6 | PLF | ( % ) | 62 | 63.3298 | 63.3298
7 | Feed Water consumption | MT | 725 | 15237 | 15237
8 | Boiler Steam Generation | MT | 685 | 14807 | 14807
9 | Bleed steam | MT | 0 | 839 | 839
10 | Turbine steam consumption | MT | 595 | 13494 | 13494
11 | Condensate Generation | MT | 522 | 11012 | 11012
12 | Auxilairy steam consumption | MT | 17 | 384 | 384
13 | Specific steam consumption | Kg/Kwhr | 3.9987 | 4.1725 | 4.1725
14 | Specific fuel consumption | Kg/Kwhr | 0.81989 | 0.88064 | 0.88064
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2693.7164 | 2811.6827 | 2811.6827
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3971.9896 | 3950.4587 | 3950.4587
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 122 | 2848 | 2848
2 | GCV ( ADB ) | Kcal/kg | 4840
WTP Report
1 | DM water Generation | m3 | 13 | 369 | 369
2 | DM water Consumption | m3 | 13 | 384 | 384
3 | CT Makeup Water Consumption | m3 | 15 | 398 | 398
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1353
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 430 | 430
6 | Fly ash to Coal yard(Truck) | nos | 5 | 52 | 52
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 23
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-23 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 132300 | 3366300 | 3366300
2 | Auxiliary power consumption | kWhr | 17208 | 394880 | 394880
3 | Net Power Exported | kWhr | 115092 | 2971420 | 2971420
4 | Auxiliary power consumption | ( % ) | 13.0068 | 11.7304 | 11.7304
5 | Average Power Generation | MWhr | 5.5125 | 6.2962 | 6.2962
6 | Plant Running Hours | Hrs | 24 | 534.66 | 534.66
6 | PLF | ( % ) | 55.125 | 62.9615 | 62.9615
7 | Feed Water consumption | MT | 667 | 15904 | 15904
8 | Boiler Steam Generation | MT | 616 | 15423 | 15423
9 | Bleed steam | MT | 0 | 839 | 839
10 | Turbine steam consumption | MT | 537 | 14031 | 14031
11 | Condensate Generation | MT | 474 | 11486 | 11486
12 | Auxilairy steam consumption | MT | 18 | 402 | 402
13 | Specific steam consumption | Kg/Kwhr | 4.059 | 4.1681 | 4.1681
14 | Specific fuel consumption | Kg/Kwhr | 0.7483 | 0.87544 | 0.87544
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2734.8526 | 2808.6632 | 2808.6632
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4017.3654 | 3953.0882 | 3953.0882
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 99 | 2947 | 2947
2 | GCV ( ADB ) | Kcal/kg | 5362
WTP Report
1 | DM water Generation | m3 | 16 | 385 | 385
2 | DM water Consumption | m3 | 14 | 398 | 398
3 | CT Makeup Water Consumption | m3 | 18 | 416 | 416
4 | Fly ash combustible/ GCV | % / kcal/kg | 23 | 1462
5 | Fly ash to cement mill | MT | 0 | 430 | 430
6 | Fly ash to Coal yard(Truck) | nos | 4 | 56 | 56
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 24
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-24 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 145700 | 3512000 | 3512000
2 | Auxiliary power consumption | kWhr | 17404 | 412284 | 412284
3 | Net Power Exported | kWhr | 128296 | 3099716 | 3099716
4 | Auxiliary power consumption | ( % ) | 11.9451 | 11.7393 | 11.7393
5 | Average Power Generation | MWhr | 6.0708 | 6.2865 | 6.2865
6 | Plant Running Hours | Hrs | 24 | 558.66 | 558.66
6 | PLF | ( % ) | 60.7083 | 62.8647 | 62.8647
7 | Feed Water consumption | MT | 695 | 16599 | 16599
8 | Boiler Steam Generation | MT | 675 | 16098 | 16098
9 | Bleed steam | MT | 2 | 841 | 841
10 | Turbine steam consumption | MT | 586 | 14617 | 14617
11 | Condensate Generation | MT | 516 | 12002 | 12002
12 | Auxilairy steam consumption | MT | 18 | 420 | 420
13 | Specific steam consumption | Kg/Kwhr | 4.022 | 4.162 | 4.162
14 | Specific fuel consumption | Kg/Kwhr | 0.72752 | 0.86931 | 0.86931
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2709.8696 | 2804.5646 | 2804.5646
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3997.281 | 3954.9216 | 3954.9216
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 106 | 3053 | 3053
2 | GCV ( ADB ) | Kcal/kg | 5463
WTP Report
1 | DM water Generation | m3 | 14 | 399 | 399
2 | DM water Consumption | m3 | 15 | 413 | 413
3 | CT Makeup Water Consumption | m3 | 17 | 433 | 433
4 | Fly ash combustible/ GCV | % / kcal/kg | 27 | 2209
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 430 | 430
6 | Fly ash to Coal yard(Truck) | nos | 4 | 60 | 60
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 25
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-25 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 155800 | 3667800 | 3667800
2 | Auxiliary power consumption | kWhr | 17634 | 429918 | 429918
3 | Net Power Exported | kWhr | 138166 | 3237882 | 3237882
4 | Auxiliary power consumption | ( % ) | 11.3184 | 11.7214 | 11.7214
5 | Average Power Generation | MWhr | 6.4917 | 6.2949 | 6.2949
6 | Plant Running Hours | Hrs | 24 | 582.66 | 582.66
6 | PLF | ( % ) | 64.9167 | 62.9492 | 62.9492
7 | Feed Water consumption | MT | 722 | 17321 | 17321
8 | Boiler Steam Generation | MT | 709 | 16807 | 16807
9 | Bleed steam | MT | 43 | 884 | 884
10 | Turbine steam consumption | MT | 637 | 15254 | 15254
11 | Condensate Generation | MT | 511 | 12513 | 12513
12 | Auxilairy steam consumption | MT | 18 | 438 | 438
13 | Specific steam consumption | Kg/Kwhr | 4.0886 | 4.1589 | 4.1589
14 | Specific fuel consumption | Kg/Kwhr | 0.82798 | 0.86755 | 0.86755
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2754.1142 | 2802.4216 | 2802.4216
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3926.4425 | 3953.7119 | 3953.7119
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 129 | 3182 | 3182
2 | GCV ( ADB ) | Kcal/kg | 4730
WTP Report
1 | DM water Generation | m3 | 14 | 413 | 413
2 | DM water Consumption | m3 | 13 | 426 | 426
3 | CT Makeup Water Consumption | m3 | 17 | 450 | 450
4 | Fly ash combustible/ GCV | % / kcal/kg | 24 | 1827
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 430 | 430
6 | Fly ash to Coalyard(Truck) | nos | 3 | 63 | 63
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 26
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-26 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 162100 | 3829900 | 3829900
2 | Auxiliary power consumption | kWhr | 17423 | 447341 | 447341
3 | Net Power Exported | kWhr | 144677 | 3382559 | 3382559
4 | Auxiliary power consumption | ( % ) | 10.7483 | 11.6802 | 11.6802
5 | Average Power Generation | MWhr | 6.7542 | 6.3131 | 6.3131
6 | Plant Running Hours | Hrs | 24 | 606.66 | 606.66
6 | PLF | ( % ) | 67.5417 | 63.1309 | 63.1309
7 | Feed Water consumption | MT | 744 | 18065 | 18065
8 | Boiler Steam Generation | MT | 731 | 17538 | 17538
9 | Bleed steam | MT | 61 | 945 | 945
10 | Turbine steam consumption | MT | 675 | 15929 | 15929
11 | Condensate Generation | MT | 525 | 13038 | 13038
12 | Auxilairy steam consumption | MT | 17 | 455 | 455
13 | Specific steam consumption | Kg/Kwhr | 4.1641 | 4.1591 | 4.1591
14 | Specific fuel consumption | Kg/Kwhr | 0.86366 | 0.86739 | 0.86739
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.2128 | 2802.5398 | 2802.5398
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3890.9426 | 3951.0552 | 3951.0552
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 3322 | 3322
2 | GCV ( ADB ) | Kcal/kg | 4501
WTP Report
1 | DM water Generation | m3 | 16 | 429 | 429
2 | DM water Consumption | m3 | 15 | 441 | 441
3 | CT Makeup Water Consumption | m3 | 17 | 467 | 467
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.6 | 1414
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 39 | 469 | 469
6 | Fly ash to Coalyard(Truck) | nos | 1 | 64 | 64
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 27
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-27 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 164500 | 3994400 | 3994400
2 | Auxiliary power consumption | kWhr | 17536 | 464877 | 464877
3 | Net Power Exported | kWhr | 146964 | 3529523 | 3529523
4 | Auxiliary power consumption | ( % ) | 10.6602 | 11.6382 | 11.6382
5 | Average Power Generation | MWhr | 6.8542 | 6.3337 | 6.3337
6 | Plant Running Hours | Hrs | 24 | 630.66 | 630.66
6 | PLF | ( % ) | 68.5417 | 63.3368 | 63.3368
7 | Feed Water consumption | MT | 755 | 18820 | 18820
8 | Boiler Steam Generation | MT | 739 | 18277 | 18277
9 | Bleed steam | MT | 63 | 1008 | 1008
10 | Turbine steam consumption | MT | 682 | 16611 | 16611
11 | Condensate Generation | MT | 533 | 13571 | 13571
12 | Auxilairy steam consumption | MT | 18 | 473 | 473
13 | Specific steam consumption | Kg/Kwhr | 4.1459 | 4.1586 | 4.1586
14 | Specific fuel consumption | Kg/Kwhr | 0.83891 | 0.86621 | 0.86621
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2793.4711 | 2802.1663 | 2802.1663
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3876.1359 | 3947.9698 | 3947.9698
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 3460 | 3460
2 | GCV ( ADB ) | Kcal/kg | 4605 | 0
WTP Report
1 | DM water Generation | m3 | 17 | 446 | 446
2 | DM water Consumption | m3 | 18 | 459 | 459
3 | CT Makeup Water Consumption | m3 | 18 | 485 | 485
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1459
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 516 | 516
6 | Fly ash to Coalyard(Truck) | nos | 0 | 64 | 64
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 28
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-28 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 162600 | 4157000 | 4157000
2 | Auxiliary power consumption | kWhr | 17389 | 482266 | 482266
3 | Net Power Exported | kWhr | 145211 | 3674734 | 3674734
4 | Auxiliary power consumption | ( % ) | 10.6943 | 11.6013 | 11.6013
5 | Average Power Generation | MWhr | 6.775 | 6.3499 | 6.3499
6 | Plant Running Hours | Hrs | 24 | 654.66 | 654.66
6 | PLF | ( % ) | 67.75 | 63.4986 | 63.4986
7 | Feed Water consumption | MT | 752 | 19572 | 19572
8 | Boiler Steam Generation | MT | 731 | 19008 | 19008
9 | Bleed steam | MT | 61 | 1069 | 1069
10 | Turbine steam consumption | MT | 680 | 17291 | 17291
11 | Condensate Generation | MT | 531 | 14102 | 14102
12 | Auxilairy steam consumption | MT | 19 | 492 | 492
13 | Specific steam consumption | Kg/Kwhr | 4.182 | 4.1595 | 4.1595
14 | Specific fuel consumption | Kg/Kwhr | 0.86101 | 0.86601 | 0.86601
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2817.8352 | 2802.7792 | 2802.7792
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3878.9778 | 3945.2712 | 3945.2712
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 3600 | 3600
2 | GCV ( ADB ) | Kcal/kg | 4470
WTP Report
1 | DM water Generation | m3 | 20 | 466 | 466
2 | DM water Consumption | m3 | 18 | 477 | 477
3 | CT Makeup Water Consumption | m3 | 16 | 501 | 501
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1548
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 541 | 541
6 | Fly ash to Coalyard(Truck) | nos | 2 | 66 | 66
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 29
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-29 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 166500 | 4323500 | 4323500
2 | Auxiliary power consumption | kWhr | 17707 | 499973 | 499973
3 | Net Power Exported | kWhr | 148793 | 3823527 | 3823527
4 | Auxiliary power consumption | ( % ) | 10.6348 | 11.5641 | 11.5641
5 | Average Power Generation | MWhr | 6.9375 | 6.3706 | 6.3706
6 | Plant Running Hours | Hrs | 24 | 678.66 | 678.66
6 | PLF | ( % ) | 69.375 | 63.7064 | 63.7064
7 | Feed Water consumption | MT | 765 | 20337 | 20337
8 | Boiler Steam Generation | MT | 746 | 19754 | 19754
9 | Bleed steam | MT | 62 | 1131 | 1131
10 | Turbine steam consumption | MT | 693 | 17984 | 17984
11 | Condensate Generation | MT | 541 | 14643 | 14643
12 | Auxilairy steam consumption | MT | 19 | 511 | 511
13 | Specific steam consumption | Kg/Kwhr | 4.1622 | 4.1596 | 4.1596
14 | Specific fuel consumption | Kg/Kwhr | 0.82883 | 0.86458 | 0.86458
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2803.6577 | 2802.813 | 2802.813
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3865.8505 | 3942.2127 | 3942.2127
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 3738 | 3738
2 | GCV ( ADB ) | Kcal/kg | 4651 | 0
WTP Report
1 | DM water Generation | m3 | 11 | 477 | 477
2 | DM water Consumption | m3 | 14 | 491 | 491
3 | CT Makeup Water Consumption | m3 | 19 | 520 | 520
4 | Fly ash combustible/ GCV | % / kcal/kg | 23 | 1520
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 54 | 595 | 595
6 | Fly ash to Coalyard(Truck) | nos | 0 | 66 | 66
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 30
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-04-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165800 | 4489300 | 4489300
2 | Auxiliary power consumption | kWhr | 17741 | 517714 | 517714
3 | Net Power Exported | kWhr | 148059 | 3971586 | 3971586
4 | Auxiliary power consumption | ( % ) | 10.7002 | 11.5322 | 11.5322
5 | Average Power Generation | MWhr | 6.9083 | 6.389 | 6.389
6 | Plant Running Hours | Hrs | 24 | 702.66 | 702.66
6 | PLF | ( % ) | 69.0833 | 63.8901 | 63.8901
7 | Feed Water consumption | MT | 762 | 21099 | 21099
8 | Boiler Steam Generation | MT | 740 | 20494 | 20494
9 | Bleed steam | MT | 61 | 1192 | 1192
10 | Turbine steam consumption | MT | 693 | 18677 | 18677
11 | Condensate Generation | MT | 538 | 15181 | 15181
12 | Auxilairy steam consumption | MT | 17 | 528 | 528
13 | Specific steam consumption | Kg/Kwhr | 4.1797 | 4.1603 | 4.1603
14 | Specific fuel consumption | Kg/Kwhr | 0.79011 | 0.86183 | 0.86183
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2815.4946 | 2803.2814 | 2803.2814
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3850.948 | 3938.842 | 3938.842
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 131 | 3869 | 3869
2 | GCV ( ADB ) | Kcal/kg | 4849
WTP Report
1 | DM water Generation | m3 | 13 | 490 | 490
2 | DM water Consumption | m3 | 14 | 505 | 505
3 | CT Makeup Water Consumption | m3 | 18 | 538 | 538
4 | Fly ash combustible/ GCV | % / kcal/kg | 26 | 1971
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 37 | 632 | 632
6 | Fly ash to Coalyard(Truck) | nos | 0 | 66 | 66
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0