## 0
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-05-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 177800 | 4799800 | 9289100
2 | Auxiliary power consumption | kWhr | 17870 | 540770 | 1058484
3 | Net Power Exported | kWhr | 159930 | 4259030 | 8230616
4 | Auxiliary power consumption | ( % ) | 10.0506 | 11.2665 | 11.3949
5 | Average Power Generation | MWhr | 7.4083 | 6.4513 | 6.4211
6 | Plant Running Hours | Hrs | 24 | 744 | 1446.66
6 | PLF | ( % ) | 74.0833 | 64.5134 | 64.2107
7 | Feed Water consumption | MT | 816 | 22589 | 43688
8 | Boiler Steam Generation | MT | 789 | 21895 | 42389
9 | Bleed steam | MT | 58 | 1253 | 2445
10 | Turbine steam consumption | MT | 744 | 19937 | 38614
11 | Condensate Generation | MT | 585 | 16025 | 31206
12 | Auxilairy steam consumption | MT | 18 | 553 | 1081
13 | Specific steam consumption | Kg/Kwhr | 4.1845 | 4.1537 | 4.1569
14 | Specific fuel consumption | Kg/Kwhr | 0.89989 | 0.8965 | 0.87974
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2818.6839 | 2798.3376 | 2800.7269
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3828.8267 | 3935.8838 | 3937.3135
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 160 | 4303 | 8172
2 | GCV ( ADB ) | Kcal/kg | 4262
WTP Report
1 | DM water Generation | m3 | 14 | 465 | 955
2 | DM water Consumption | m3 | 15 | 462 | 967
3 | CT Makeup Water Consumption | m3 | 18 | 598 | 1136
4 | Fly ash combustible/ GCV | % / kcal/kg | 0 | 0
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 36 | 739 | 1371
6 | Fly ash to Coalyard(Truck) | nos | 2 | 89 | 155
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 1
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-01 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 181500 | 181500 | 9470600
2 | Auxiliary power consumption | kWhr | 17898 | 17898 | 1076382
3 | Net Power Exported | kWhr | 163602 | 163602 | 8394218
4 | Auxiliary power consumption | ( % ) | 9.8612 | 9.8612 | 11.3655
5 | Average Power Generation | MWhr | 7.5625 | 7.5625 | 6.4397
6 | Plant Running Hours | Hrs | 24 | 24 | 1470.66
6 | PLF | ( % ) | 75.625 | 75.625 | 64.3969
7 | Feed Water consumption | MT | 824 | 824 | 44512
8 | Boiler Steam Generation | MT | 803 | 803 | 43192
9 | Bleed steam | MT | 61 | 61 | 2506
10 | Turbine steam consumption | MT | 759 | 759 | 39373
11 | Condensate Generation | MT | 591 | 591 | 31797
12 | Auxilairy steam consumption | MT | 18 | 18 | 1099
13 | Specific steam consumption | Kg/Kwhr | 4.1818 | 4.1818 | 4.1574
14 | Specific fuel consumption | Kg/Kwhr | 0.8595 | 0.8595 | 0.87935
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.3471 | 2816.3471 | 2801.0262
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.3271 | 3817.3271 | 3935.014
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 156 | 156 | 8328
2 | GCV ( ADB ) | Kcal/kg | 4405
WTP Report
1 | DM water Generation | m2 | 13 | 13 | 968
2 | DM water Consumption | m3 | 12 | 12 | 979
3 | CT Makeup Water Consumption | m3 | 18 | 18 | 1154
4 | Fly ash combustible/ GCV | % / kcal/kg | 21.7 | 1423
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 40 | 40 | 1411
6 | Fly ash to Coal yard(Truck) | nos | 1 | 1 | 156
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 2
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-02 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 139400 | 320900 | 9610000
2 | Auxiliary power consumption | kWhr | 17330 | 35228 | 1093712
3 | Net Power Exported | kWhr | 122070 | 285672 | 8516288
4 | Auxiliary power consumption | ( % ) | 12.4319 | 10.9779 | 11.381
5 | Average Power Generation | MWhr | 5.8083 | 6.6854 | 6.4296
6 | Plant Running Hours | Hrs | 24 | 48 | 1494.66
7 | PLF | ( % ) | 58.0833 | 66.8542 | 64.2956
8 | Feed Water consumption | MT | 679 | 1503 | 45191
9 | Boiler Steam Generation | MT | 650 | 1453 | 43842
10 | Bleed steam | MT | 26 | 87 | 2532
11 | Turbine steam consumption | MT | 581 | 1340 | 39954
12 | Condensate Generation | MT | 480 | 1071 | 32277
13 | Auxilairy steam consumption | MT | 18 | 36 | 1117
14 | Specific steam consumption | Kg/Kwhr | 4.1679 | 4.1758 | 4.1575
15 | Specific fuel consumption | Kg/Kwhr | 0.93257 | 0.89124 | 0.88012
16 | Heat Rate(TG)2880 | Kcal/Kwh | 2807.9842 | 2812.7142 | 2801.1272
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4023.1946 | 3906.7566 | 3936.2931
18 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 130 | 286 | 8458
2 | GCV ( ADB ) | Kcal/kg | 4300
WTP Report
1 | DM water Generation | m3 | 13 | 26 | 981
2 | DM water Consumption | m3 | 14 | 26 | 993
3 | CT Makeup Water Consumption | m3 | 18 | 36 | 1172
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1423
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 87 | 1458
6 | Fly ash to Coal yard(Truck) | nos | 0 | 1 | 156
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 3
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-03 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 152575 | 473475 | 9762575
2 | Auxiliary power consumption | kWhr | 17683 | 52911 | 1111395
3 | Net Power Exported | kWhr | 134892 | 420564 | 8651180
4 | Auxiliary power consumption | ( % ) | 11.5897 | 11.175 | 11.3842
5 | Average Power Generation | MWhr | 6.3573 | 6.576 | 6.4284
6 | Plant Running Hours | Hrs | 24 | 72 | 1518.66
6 | PLF | ( % ) | 63.5729 | 65.7604 | 64.2841
7 | Feed Water consumption | MT | 724 | 2227 | 45915
8 | Boiler Steam Generation | MT | 695 | 2148 | 44537
9 | Bleed steam | MT | 45 | 132 | 2577
10 | Turbine steam consumption | MT | 637 | 1977 | 40591
11 | Condensate Generation | MT | 512 | 1583 | 32789
12 | Auxilairy steam consumption | MT | 17 | 53 | 1134
13 | Specific steam consumption | Kg/Kwhr | 4.175 | 4.1755 | 4.1578
14 | Specific fuel consumption | Kg/Kwhr | 0.90447 | 0.89551 | 0.88051
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2813.5081 | 2812.9701 | 2801.3207
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3930.2655 | 3914.3322 | 3936.1989
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 424 | 8596
2 | GCV ( ADB ) | Kcal/kg | 4327
WTP Report
1 | DM water Generation | m3 | 19 | 45 | 1000
2 | DM water Consumption | m3 | 19 | 45 | 1012
3 | CT Makeup Water Consumption | m3 | 18 | 54 | 1190
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1324
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 87 | 1458
6 | Fly ash to Coal yard(Truck) | nos | 3 | 4 | 159
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 4
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-04 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178200 | 651675 | 9940775
2 | Auxiliary power consumption | kWhr | 18270 | 71181 | 1129665
3 | Net Power Exported | kWhr | 159930 | 580494 | 8811110
4 | Auxiliary power consumption | ( % ) | 10.2525 | 10.9228 | 11.364
5 | Average Power Generation | MWhr | 7.425 | 6.7883 | 6.4439
6 | Plant Running Hours | Hrs | 24 | 96 | 1542.66
6 | PLF | ( % ) | 74.25 | 67.8828 | 64.4392
7 | Feed Water consumption | MT | 810 | 3037 | 46725
8 | Boiler Steam Generation | MT | 790 | 2938 | 45327
9 | Bleed steam | MT | 67 | 199 | 2644
10 | Turbine steam consumption | MT | 742 | 2719 | 41333
11 | Condensate Generation | MT | 576 | 2159 | 33365
12 | Auxilairy steam consumption | MT | 18 | 71 | 1152
13 | Specific steam consumption | Kg/Kwhr | 4.1639 | 4.1723 | 4.1579
14 | Specific fuel consumption | Kg/Kwhr | 0.88664 | 0.89308 | 0.88062
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2804.6352 | 2810.6909 | 2801.3801
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3825.0741 | 3889.9247 | 3934.2069
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 158 | 582 | 8754
2 | GCV ( ADB ) | Kcal/kg | 4310
WTP Report
1 | DM water Generation | m3 | 14 | 59 | 1014
2 | DM water Consumption | m3 | 14 | 59 | 1026
3 | CT Makeup Water Consumption | m3 | 7 | 61 | 1197
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1322
5 | Fly ash to cement mill | MT | 56 | 143 | 1514
6 | Fly ash to Coal yard(Truck) | nos | 0 | 4 | 159
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 5
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-05 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 161100 | 812775 | 10101875
2 | Auxiliary power consumption | kWhr | 17959 | 89140 | 1147624
3 | Net Power Exported | kWhr | 143141 | 723635 | 8954251
4 | Auxiliary power consumption | ( % ) | 11.1477 | 10.9674 | 11.3605
5 | Average Power Generation | MWhr | 6.7125 | 6.7731 | 6.448
6 | Plant Running Hours | Hrs | 24 | 120 | 1566.66
6 | PLF | ( % ) | 67.125 | 67.7313 | 64.4803
7 | Feed Water consumption | MT | 745 | 3782 | 47470
8 | Boiler Steam Generation | MT | 715 | 3653 | 46042
9 | Bleed steam | MT | 58 | 257 | 2702
10 | Turbine steam consumption | MT | 677 | 3396 | 42010
11 | Condensate Generation | MT | 528 | 2687 | 33893
12 | Auxilairy steam consumption | MT | 18 | 89 | 1170
13 | Specific steam consumption | Kg/Kwhr | 4.2024 | 4.1783 | 4.1586
14 | Specific fuel consumption | Kg/Kwhr | 0.86903 | 0.88831 | 0.88043
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2830.7945 | 2814.6756 | 2801.8492
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3829.402 | 3877.9285 | 3932.5355
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 722 | 8894
2 | GCV ( ADB ) | Kcal/kg | 4369
WTP Report
1 | DM water Generation | m3 | 13 | 72 | 1027
2 | DM water Consumption | m3 | 14 | 73 | 1040
3 | CT Makeup Water Consumption | m3 | 35 | 96 | 1232
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1391
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 30 | 173 | 1544
6 | Fly ash to Coal yard(Truck) | nos | 0 | 4 | 159
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 6
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-06 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 157200 | 969975 | 10259075
2 | Auxiliary power consumption | kWhr | 17838 | 106978 | 1165462
3 | Net Power Exported | kWhr | 139362 | 862997 | 9093613
4 | Auxiliary power consumption | ( % ) | 11.3473 | 11.0289 | 11.3603
5 | Average Power Generation | MWhr | 6.55 | 6.7359 | 6.4496
6 | Plant Running Hours | Hrs | 24 | 144 | 1590.66
6 | PLF | ( % ) | 65.5 | 67.3594 | 64.4957
7 | Feed Water consumption | MT | 727 | 4509 | 48197
8 | Boiler Steam Generation | MT | 706 | 4359 | 46748
9 | Bleed steam | MT | 52 | 309 | 2754
10 | Turbine steam consumption | MT | 655 | 4051 | 42665
11 | Condensate Generation | MT | 515 | 3202 | 34408
12 | Auxilairy steam consumption | MT | 17 | 106 | 1187
13 | Specific steam consumption | Kg/Kwhr | 4.1667 | 4.1764 | 4.1588
14 | Specific fuel consumption | Kg/Kwhr | 0.89059 | 0.88868 | 0.88059
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.8384 | 2813.4055 | 2801.9256
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3875.0082 | 3877.4552 | 3931.654
17 | DG Power Generation | kWhr |  | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 862 | 9034
2 | GCV ( ADB ) | Kcal/kg | 4320
WTP Report
1 | DM water Generation | m3 | 15 | 87 | 1042
2 | DM water Consumption | m3 | 14 | 87 | 1054
3 | CT Makeup Water Consumption | m3 | 45 | 141 | 1277
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1403
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 198 | 1569
6 | Fly ash to Coal yard(Truck) | nos | 3 | 7 | 162
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 7
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-07 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 157900 | 1127875 | 10416975
2 | Auxiliary power consumption | kWhr | 17849 | 124827 | 1183311
3 | Net Power Exported | kWhr | 140051 | 1003048 | 9233664
4 | Auxiliary power consumption | ( % ) | 11.304 | 11.0674 | 11.3594
5 | Average Power Generation | MWhr | 6.5792 | 6.7135 | 6.4515
6 | Plant Running Hours | Hrs | 24 | 168 | 1614.66
6 | PLF | ( % ) | 65.7917 | 67.1354 | 64.515
7 | Feed Water consumption | MT | 727 | 5236 | 48924
8 | Boiler Steam Generation | MT | 700 | 5059 | 47448
9 | Bleed steam | MT | 56 | 365 | 2810
10 | Turbine steam consumption | MT | 661 | 4712 | 43326
11 | Condensate Generation | MT | 514 | 3716 | 34922
12 | Auxilairy steam consumption | MT | 18 | 124 | 1205
13 | Specific steam consumption | Kg/Kwhr | 4.1862 | 4.1778 | 4.1592
14 | Specific fuel consumption | Kg/Kwhr | 0.87397 | 0.88662 | 0.88049
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2820.1583 | 2814.3509 | 2802.202
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3825.0434 | 3870.1177 | 3930.038
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 138 | 1000 | 9172
2 | GCV ( ADB ) | Kcal/kg | 4342
1 | DM water Generation | m3 | 14 | 101 | 1056
2 | DM water Consumption | m3 | 15 | 102 | 1069
3 | CT Makeup Water Consumption | m3 | 18 | 159 | 1295
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.85 | 1392
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 30 | 228 | 1599
6 | Fly ash to Coal yard(Truck) | nos | 2 | 9 | 164
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 8
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-08 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 155600 | 1283475 | 10572575
2 | Auxiliary power consumption | kWhr | 17873 | 142700 | 1201184
3 | Net Power Exported | kWhr | 137727 | 1140775 | 9371391
4 | Auxiliary power consumption | ( % ) | 11.4865 | 11.1183 | 11.3613
5 | Average Power Generation | MWhr | 6.4833 | 6.6848 | 6.452
6 | Plant Running Hours | Hrs | 24 | 192 | 1638.66
6 | PLF | ( % ) | 64.8333 | 66.8477 | 64.5196
7 | Feed Water consumption | MT | 717 | 5953 | 49641
8 | Boiler Steam Generation | MT | 692 | 5751 | 48140
9 | Bleed steam | MT | 54 | 419 | 2864
10 | Turbine steam consumption | MT | 648 | 5360 | 43974
11 | Condensate Generation | MT | 507 | 4223 | 35429
12 | Auxilairy steam consumption | MT | 18 | 142 | 1223
13 | Specific steam consumption | Kg/Kwhr | 4.1645 | 4.1762 | 4.1593
14 | Specific fuel consumption | Kg/Kwhr | 0.88046 | 0.88588 | 0.88049
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.4242 | 2813.2687 | 2802.2494
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3837.2223 | 3866.1297 | 3928.672
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 137 | 1137 | 9309
2 | GCV ( ADB ) | Kcal/kg | 4350
WTP Report
1 | DM water Generation | m3 | 15 | 116 | 1071
2 | DM water Consumption | m3 | 14 | 116 | 1083
3 | CT Makeup Water Consumption | m3 | 17 | 176 | 1312
4 | Fly ash combustible/ GCV | % / kcal/kg | 19.38 | 1389
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 10 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 4 | 13 | 168
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 9
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-09 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 160200 | 1443675 | 10732775
2 | Auxiliary power consumption | kWhr | 17769 | 160469 | 1218953
3 | Net Power Exported | kWhr | 142431 | 1283206 | 9513822
4 | Auxiliary power consumption | ( % ) | 11.0918 | 11.1153 | 11.3573
5 | Average Power Generation | MWhr | 6.675 | 6.6837 | 6.4552
6 | Plant Running Hours | Hrs | 24 | 216 | 1662.66
6 | PLF | ( % ) | 66.75 | 66.8368 | 64.5518
7 | Feed Water consumption | MT | 740 | 6693 | 50381
8 | Boiler Steam Generation | MT | 712 | 6463 | 48852
9 | Bleed steam | MT | 57 | 476 | 2921
10 | Turbine steam consumption | MT | 670 | 6030 | 44644
11 | Condensate Generation | MT | 523 | 4746 | 35952
12 | Auxilairy steam consumption | MT | 18 | 160 | 1241
13 | Specific steam consumption | Kg/Kwhr | 4.1823 | 4.1768 | 4.1596
14 | Specific fuel consumption | Kg/Kwhr | 0.81149 | 0.87762 | 0.87946
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2818.04 | 2813.7981 | 2802.4851
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3834.7578 | 3862.6484 | 3927.2702
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 130 | 1267 | 9439
2 | GCV ( ADB ) | Kcal/kg | 4693
WTP Report
1 | DM water Generation | m3 | 14 | 130 | 1085
2 | DM water Consumption | m3 | 18 | 134 | 1101
3 | CT Makeup Water Consumption | m3 | 18 | 194 | 1330
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1439
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 18 | 173
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 10
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-10 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 163000 | 1606675 | 10895775
2 | Auxiliary power consumption | kWhr | 17865 | 178334 | 1236818
3 | Net Power Exported | kWhr | 145135 | 1428341 | 9658957
4 | Auxiliary power consumption | ( % ) | 10.9601 | 11.0996 | 11.3514
5 | Average Power Generation | MWhr | 6.7917 | 6.6945 | 6.46
6 | Plant Running Hours | Hrs | 24 | 240 | 1686.66
6 | PLF | ( % ) | 67.9167 | 66.9448 | 64.5997
7 | Feed Water consumption | MT | 748 | 7441 | 51129
8 | Boiler Steam Generation | MT | 729 | 7192 | 49581
9 | Bleed steam | MT | 58 | 534 | 2979
10 | Turbine steam consumption | MT | 679 | 6709 | 45323
11 | Condensate Generation | MT | 530 | 5276 | 36482
12 | Auxilairy steam consumption | MT | 17 | 177 | 1258
13 | Specific steam consumption | Kg/Kwhr | 4.1656 | 4.1757 | 4.1597
14 | Specific fuel consumption | Kg/Kwhr | 0.80368 | 0.87012 | 0.87832
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.8712 | 2812.9939 | 2802.5358
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3858.8721 | 3862.2653 | 3926.247
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 131 | 1398 | 9570
2 | GCV ( ADB ) | Kcal/kg | 4798
WTP Report
1 | DM water Generation | m3 | 11 | 141 | 1096
2 | DM water Consumption | m3 | 13 | 147 | 1114
3 | CT Makeup Water Consumption | m3 | 18 | 212 | 1348
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1426
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 4 | 22 | 177
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 11
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-11 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 156800 | 1763475 | 11052575
2 | Auxiliary power consumption | kWhr | 17906 | 196240 | 1254724
3 | Net Power Exported | kWhr | 138894 | 1567235 | 9797851
4 | Auxiliary power consumption | ( % ) | 11.4196 | 11.128 | 11.3523
5 | Average Power Generation | MWhr | 6.5333 | 6.6798 | 6.461
6 | Plant Running Hours | Hrs | 24 | 264 | 1710.66
6 | PLF | ( % ) | 65.3333 | 66.7983 | 64.61
7 | Feed Water consumption | MT | 739 | 8180 | 51868
8 | Boiler Steam Generation | MT | 704 | 7896 | 50285
9 | Bleed steam | MT | 52 | 586 | 3031
10 | Turbine steam consumption | MT | 658 | 7367 | 45981
11 | Condensate Generation | MT | 523 | 5799 | 37005
12 | Auxilairy steam consumption | MT | 18 | 195 | 1276
13 | Specific steam consumption | Kg/Kwhr | 4.1964 | 4.1775 | 4.1602
14 | Specific fuel consumption | Kg/Kwhr | 0.87372 | 0.87044 | 0.87826
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2827.2577 | 2814.2622 | 2802.8865
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3873.888 | 3863.2988 | 3925.5042
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 137 | 1535 | 9707
2 | GCV ( ADB ) | Kcal/kg | 4411
WTP Report
1 | DM water Generation | m3 | 17 | 158 | 1113
2 | DM water Consumption | m3 | 16 | 163 | 1130
3 | CT Makeup Water Consumption | m3 | 20 | 232 | 1368
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1420
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 27 | 182
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 12
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-12 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 158600 | 1922075 | 11211175
2 | Auxiliary power consumption | kWhr | 17938 | 214178 | 1272662
3 | Net Power Exported | kWhr | 140662 | 1707897 | 9938513
4 | Auxiliary power consumption | ( % ) | 11.3102 | 11.1431 | 11.3517
5 | Average Power Generation | MWhr | 6.6083 | 6.6739 | 6.463
6 | Plant Running Hours | Hrs | 24 | 288 | 1734.66
6 | PLF | ( % ) | 66.0833 | 66.7387 | 64.6304
7 | Feed Water consumption | MT | 733 | 8913 | 52601
8 | Boiler Steam Generation | MT | 710 | 8606 | 50995
9 | Bleed steam | MT | 54 | 640 | 3085
10 | Turbine steam consumption | MT | 664 | 8031 | 46645
11 | Condensate Generation | MT | 520 | 6319 | 37525
12 | Auxilairy steam consumption | MT | 18 | 213 | 1294
13 | Specific steam consumption | Kg/Kwhr | 4.1866 | 4.1783 | 4.1606
14 | Specific fuel consumption | Kg/Kwhr | 0.86381 | 0.86989 | 0.87805
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2821.0088 | 2814.8189 | 2803.1428
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3862.5635 | 3863.2381 | 3924.6138
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 137 | 1672 | 9844
2 | GCV ( ADB ) | Kcal/kg | 4450
WTP Report
1 | DM water Generation | m3 | 17 | 175 | 1130
2 | DM water Consumption | m3 | 18 | 181 | 1148
3 | CT Makeup Water Consumption | m3 | 18 | 250 | 1386
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1449
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 32 | 187
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 13
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-13 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 144100 | 2066175 | 11355275
2 | Auxiliary power consumption | kWhr | 17641 | 231819 | 1290303
3 | Net Power Exported | kWhr | 126459 | 1834356 | 10064972
4 | Auxiliary power consumption | ( % ) | 12.2422 | 11.2197 | 11.363
5 | Average Power Generation | MWhr | 6.0042 | 6.6224 | 6.4568
6 | Plant Running Hours | Hrs | 24 | 312 | 1758.66
6 | PLF | ( % ) | 60.0417 | 66.2236 | 64.5678
7 | Feed Water consumption | MT | 689 | 9602 | 53290
8 | Boiler Steam Generation | MT | 660 | 9266 | 51655
9 | Bleed steam | MT | 32 | 672 | 3117
10 | Turbine steam consumption | MT | 597 | 8628 | 47242
11 | Condensate Generation | MT | 519 | 6838 | 38044
12 | Auxilairy steam consumption | MT | 18 | 231 | 1312
13 | Specific steam consumption | Kg/Kwhr | 4.143 | 4.1758 | 4.1604
14 | Specific fuel consumption | Kg/Kwhr | 0.87439 | 0.87021 | 0.87801
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2792.1652 | 2813.239 | 2803.0035
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3951.8497 | 3869.4181 | 3924.9594
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 126 | 1798 | 9970
2 | GCV ( ADB ) | Kcal/kg | 4510
WTP Report
1 | DM water Generation | m3 | 18 | 193 | 1148
2 | DM water Consumption | m3 | 19 | 200 | 1167
3 | CT Makeup Water Consumption | m3 | 18 | 268 | 1404
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1412
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 4 | 36 | 191
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 14
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-14 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 151800 | 2217975 | 11507075
2 | Auxiliary power consumption | kWhr | 17947 | 249766 | 1308250
3 | Net Power Exported | kWhr | 133853 | 1968209 | 10198825
4 | Auxiliary power consumption | ( % ) | 11.8228 | 11.261 | 11.3691
5 | Average Power Generation | MWhr | 6.325 | 6.6011 | 6.455
6 | Plant Running Hours | Hrs | 24 | 336 | 1782.66
6 | PLF | ( % ) | 63.25 | 66.0112 | 64.55
7 | Feed Water consumption | MT | 724 | 10326 | 54014
8 | Boiler Steam Generation | MT | 697 | 9963 | 52352
9 | Bleed steam | MT | 31 | 703 | 3148
10 | Turbine steam consumption | MT | 626 | 9254 | 47868
11 | Condensate Generation | MT | 537 | 7375 | 38581
12 | Auxilairy steam consumption | MT | 18 | 249 | 1330
13 | Specific steam consumption | Kg/Kwhr | 4.1238 | 4.1723 | 4.1599
14 | Specific fuel consumption | Kg/Kwhr | 0.85639 | 0.86926 | 0.87772
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2777.9183 | 2810.8216 | 2802.6726
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3961.6989 | 3875.7338 | 3925.4441
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 130 | 1928 | 10100
2 | GCV ( ADB ) | Kcal/kg | 4622
WTP Report
1 | DM water Generation | m3 | 16 | 209 | 1164
2 | DM water Consumption | m3 | 13 | 213 | 1180
3 | CT Makeup Water Consumption | m3 | 10 | 278 | 1414
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.8 | 1387
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 41 | 196
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 15
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-15 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176400 | 2394375 | 11683475
2 | Auxiliary power consumption | kWhr | 18560 | 268326 | 1326810
3 | Net Power Exported | kWhr | 157840 | 2126049 | 10356665
4 | Auxiliary power consumption | ( % ) | 10.5215 | 11.2065 | 11.3563
5 | Average Power Generation | MWhr | 7.35 | 6.651 | 6.4669
6 | Plant Running Hours | Hrs | 24 | 360 | 1806.66
6 | PLF | ( % ) | 73.5 | 66.5104 | 64.6689
7 | Feed Water consumption | MT | 808 | 11134 | 54822
8 | Boiler Steam Generation | MT | 785 | 10748 | 53137
9 | Bleed steam | MT | 59 | 762 | 3207
10 | Turbine steam consumption | MT | 735 | 9989 | 48603
11 | Condensate Generation | MT | 580 | 7955 | 39161
12 | Auxilairy steam consumption | MT | 17 | 266 | 1347
13 | Specific steam consumption | Kg/Kwhr | 4.1667 | 4.1719 | 4.16
14 | Specific fuel consumption | Kg/Kwhr | 0.83333 | 0.86661 | 0.87705
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2807.0578 | 2810.5443 | 2802.7388
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3839.6491 | 3873.0754 | 3924.1487
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 147 | 2075 | 10247
2 | GCV ( ADB ) | Kcal/kg | 4587
WTP Report
1 | DM water Generation | m3 | 16 | 225 | 1180
2 | DM water Consumption | m3 | 17 | 230 | 1197
3 | CT Makeup Water Consumption | m3 | 18 | 296 | 1432
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1468
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 46 | 201
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 16
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-16 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 207600 | 2601975 | 11891075
2 | Auxiliary power consumption | kWhr | 19101 | 287427 | 1345911
3 | Net Power Exported | kWhr | 188499 | 2314548 | 10545164
4 | Auxiliary power consumption | ( % ) | 9.2009 | 11.0465 | 11.3187
5 | Average Power Generation | MWhr | 8.65 | 6.776 | 6.4955
6 | Plant Running Hours | Hrs | 24 | 384 | 1830.66
6 | PLF | ( % ) | 86.5 | 67.7598 | 64.9551
7 | Feed Water consumption | MT | 939 | 12073 | 55761
8 | Boiler Steam Generation | MT | 906 | 11654 | 54043
9 | Bleed steam | MT | 75 | 837 | 3282
10 | Turbine steam consumption | MT | 867 | 10856 | 49470
11 | Condensate Generation | MT | 679 | 8634 | 39840
12 | Auxilairy steam consumption | MT | 19 | 285 | 1366
13 | Specific steam consumption | Kg/Kwhr | 4.1763 | 4.1722 | 4.1603
14 | Specific fuel consumption | Kg/Kwhr | 0.82852 | 0.86357 | 0.8762
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.6734 | 2810.7142 | 2802.9123
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3765.4884 | 3864.4915 | 3921.3788
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 172 | 2247 | 10419
2 | GCV ( ADB ) | Kcal/kg | 4527
WTP Report
1 | DM water Generation | m3 | 14 | 239 | 1194
2 | DM water Consumption | m3 | 14 | 244 | 1211
3 | CT Makeup Water Consumption | m3 | 18 | 314 | 1450
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1358
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 5 | 51 | 206
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 17
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-17 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 190000 | 2791975 | 12081075
2 | Auxiliary power consumption | kWhr | 18408 | 305835 | 1364319
3 | Net Power Exported | kWhr | 171592 | 2486140 | 10716756
4 | Auxiliary power consumption | ( % ) | 9.6884 | 10.9541 | 11.293
5 | Average Power Generation | MWhr | 7.9167 | 6.8431 | 6.5139
6 | Plant Running Hours | Hrs | 24 | 408 | 1854.66
6 | PLF | ( % ) | 79.1667 | 68.4308 | 65.139
7 | Feed Water consumption | MT | 866 | 12939 | 56627
8 | Boiler Steam Generation | MT | 838 | 12492 | 54881
9 | Bleed steam | MT | 65 | 902 | 3347
10 | Turbine steam consumption | MT | 791 | 11647 | 50261
11 | Condensate Generation | MT | 624 | 9258 | 40464
12 | Auxilairy steam consumption | MT | 17 | 302 | 1383
13 | Specific steam consumption | Kg/Kwhr | 4.1632 | 4.1716 | 4.1603
14 | Specific fuel consumption | Kg/Kwhr | 0.81579 | 0.86032 | 0.87525
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2804.1737 | 2810.2691 | 2802.9321
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3805.4926 | 3860.4765 | 3919.5562
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 155 | 2402 | 10574
2 | GCV ( ADB ) | Kcal/kg | 4672
WTP Report
1 | DM water Generation | m3 | 14 | 253 | 1208
2 | DM water Consumption | m3 | 15 | 259 | 1226
3 | CT Makeup Water Consumption | m3 | 20 | 334 | 1470
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1362
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 238 | 1609
6 | Fly ash to Coal yard(Truck) | nos | 4 | 55 | 210
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 18
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-18 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 200400 | 2992375 | 12281475
2 | Auxiliary power consumption | kWhr | 18940 | 324775 | 1383259
3 | Net Power Exported | kWhr | 181460 | 2667600 | 10898216
4 | Auxiliary power consumption | ( % ) | 9.4511 | 10.8534 | 11.263
5 | Average Power Generation | MWhr | 8.35 | 6.9268 | 6.5374
6 | Plant Running Hours | Hrs | 24 | 432 | 1878.66
6 | PLF | ( % ) | 83.5 | 69.2679 | 65.3736
7 | Feed Water consumption | MT | 909 | 13848 | 57536
8 | Boiler Steam Generation | MT | 880 | 13372 | 55761
9 | Bleed steam | MT | 70 | 972 | 3417
10 | Turbine steam consumption | MT | 838 | 12485 | 51099
11 | Condensate Generation | MT | 656 | 9914 | 41120
12 | Auxilairy steam consumption | MT | 18 | 320 | 1401
13 | Specific steam consumption | Kg/Kwhr | 4.1816 | 4.1723 | 4.1607
14 | Specific fuel consumption | Kg/Kwhr | 0.81836 | 0.85751 | 0.87432
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.3373 | 2810.6755 | 2803.1508
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3788.8326 | 3855.6785 | 3917.4232
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 164 | 2566 | 10738
2 | GCV ( ADB ) | Kcal/kg | 4616
WTP Report
1 | DM water Generation | m3 | 13 | 266 | 1221
2 | DM water Consumption | m3 | 14 | 273 | 1240
3 | CT Makeup Water Consumption | m3 | 17 | 351 | 1487
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1323
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 29 | 267 | 1638
6 | Fly ash to Coal yard(Truck) | nos | 2 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 19
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-19 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 207600 | 3199975 | 12489075
2 | Auxiliary power consumption | kWhr | 19377 | 344152 | 1402636
3 | Net Power Exported | kWhr | 188223 | 2855823 | 11086439
4 | Auxiliary power consumption | ( % ) | 9.3338 | 10.7548 | 11.2309
5 | Average Power Generation | MWhr | 8.65 | 7.0175 | 6.564
6 | Plant Running Hours | Hrs | 24 | 456 | 1902.66
6 | PLF | ( % ) | 86.5 | 70.1749 | 65.6401
7 | Feed Water consumption | MT | 940 | 14788 | 58476
8 | Boiler Steam Generation | MT | 907 | 14279 | 56668
9 | Bleed steam | MT | 70 | 1042 | 3487
10 | Turbine steam consumption | MT | 858 | 13343 | 51957
11 | Condensate Generation | MT | 684 | 10598 | 41804
12 | Auxilairy steam consumption | MT | 18 | 338 | 1419
13 | Specific steam consumption | Kg/Kwhr | 4.1329 | 4.1697 | 4.1602
14 | Specific fuel consumption | Kg/Kwhr | 0.82852 | 0.85563 | 0.87356
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2784.2197 | 2808.9591 | 2802.8362
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3769.6445 | 3850.097 | 3914.9667
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 172 | 2738 | 10910
2 | GCV ( ADB ) | Kcal/kg | 4529
WTP Report
1 | DM water Generation | m3 | 18 | 284 | 1239
2 | DM water Consumption | m3 | 19 | 292 | 1259
3 | CT Makeup Water Consumption | m3 | 18 | 369 | 1505
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1398
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 53 | 320 | 1691
6 | Fly ash to Coal yard(Truck) | nos | 0 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 20
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-20 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 195200 | 3395175 | 12684275
2 | Auxiliary power consumption | kWhr | 18903 | 363055 | 1421539
3 | Net Power Exported | kWhr | 176297 | 3032120 | 11262736
4 | Auxiliary power consumption | ( % ) | 9.6839 | 10.6933 | 11.2071
5 | Average Power Generation | MWhr | 8.1333 | 7.0733 | 6.5836
6 | Plant Running Hours | Hrs | 24 | 480 | 1926.66
6 | PLF | ( % ) | 81.3333 | 70.7328 | 65.8356
7 | Feed Water consumption | MT | 885 | 15673 | 59361
8 | Boiler Steam Generation | MT | 858 | 15137 | 57526
9 | Bleed steam | MT | 63 | 1105 | 3550
10 | Turbine steam consumption | MT | 810 | 14153 | 52767
11 | Condensate Generation | MT | 643 | 11241 | 42447
12 | Auxilairy steam consumption | MT | 17 | 355 | 1436
13 | Specific steam consumption | Kg/Kwhr | 4.1496 | 4.1686 | 4.16
14 | Specific fuel consumption | Kg/Kwhr | 0.87602 | 0.8568 | 0.8736
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2794.9795 | 2808.1554 | 2802.7153
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3792.5205 | 3846.7867 | 3913.0824
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 171 | 2909 | 11081
2 | GCV ( ADB ) | Kcal/kg | 4334 | 0
WTP Report
1 | DM water Generation | m3 | 17 | 301 | 1256
2 | DM water Consumption | m3 | 15 | 307 | 1274
3 | CT Makeup Water Consumption | m3 | 18 | 387 | 1523
4 | Fly ash combustible/ GCV | % / kcal/kg | 17.51 | 1341
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 60 | 380 | 1751
6 | Fly ash to Coal yard(Truck) | nos | 0 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 21
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-21 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 189200 | 3584375 | 12873475
2 | Auxiliary power consumption | kWhr | 18882 | 381937 | 1440421
3 | Net Power Exported | kWhr | 170318 | 3202438 | 11433054
4 | Auxiliary power consumption | ( % ) | 9.9799 | 10.6556 | 11.1891
5 | Average Power Generation | MWhr | 7.8833 | 7.1119 | 6.5995
6 | Plant Running Hours | Hrs | 24 | 504 | 1950.66
6 | PLF | ( % ) | 78.8333 | 71.1186 | 65.9955
7 | Feed Water consumption | MT | 873 | 16546 | 60234
8 | Boiler Steam Generation | MT | 842 | 15979 | 58368
9 | Bleed steam | MT | 64 | 1169 | 3614
10 | Turbine steam consumption | MT | 792 | 14945 | 53559
11 | Condensate Generation | MT | 632 | 11873 | 43079
12 | Auxilairy steam consumption | MT | 19 | 374 | 1455
13 | Specific steam consumption | Kg/Kwhr | 4.186 | 4.1695 | 4.1604
14 | Specific fuel consumption | Kg/Kwhr | 0.7611 | 0.85175 | 0.87195
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2819.9049 | 2808.7756 | 2802.9679
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3839.8249 | 3846.4192 | 3912.0057
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 144 | 3053 | 11225
2 | GCV ( ADB ) | Kcal/kg | 5030
1 | DM water Generation | m3 | 16 | 317 | 1272
2 | DM water Consumption | m3 | 17 | 324 | 1291
3 | CT Makeup Water Consumption | m3 | 18 | 405 | 1541
4 | Fly ash combustible/ GCV | % / kcal/kg | 14 | 1125
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 41 | 421 | 1792
6 | Fly ash to Coal yard(Truck) | nos | 0 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 22
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-22 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 186200 | 3770575 | 13059675
2 | Auxiliary power consumption | kWhr | 18623 | 400560 | 1459044
3 | Net Power Exported | kWhr | 167577 | 3370015 | 11600631
4 | Auxiliary power consumption | ( % ) | 10.0016 | 10.6233 | 11.1721
5 | Average Power Generation | MWhr | 7.7583 | 7.1412 | 6.6136
6 | Plant Running Hours | Hrs | 24 | 528 | 1974.66
6 | PLF | ( % ) | 77.5833 | 71.4124 | 66.1363
7 | Feed Water consumption | MT | 865 | 17411 | 61099
8 | Boiler Steam Generation | MT | 831 | 16810 | 59199
9 | Bleed steam | MT | 67 | 1236 | 3681
10 | Turbine steam consumption | MT | 781 | 15726 | 54340
11 | Condensate Generation | MT | 622 | 12495 | 43701
12 | Auxilairy steam consumption | MT | 17 | 391 | 1472
13 | Specific steam consumption | Kg/Kwhr | 4.1944 | 4.1707 | 4.1609
14 | Specific fuel consumption | Kg/Kwhr | 0.86466 | 0.85239 | 0.87184
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2825.9023 | 2809.6213 | 2803.2949
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3850.7188 | 3846.6316 | 3911.1319
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 161 | 3214 | 11386
2 | GCV ( ADB ) | Kcal/kg | 4445
WTP Report
1 | DM water Generation | m3 | 20 | 337 | 1292
2 | DM water Consumption | m3 | 19 | 343 | 1310
3 | CT Makeup Water Consumption | m3 | 18 | 423 | 1559
4 | Fly ash combustible/ GCV | % / kcal/kg | 12 | 877
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 54 | 475 | 1846
6 | Fly ash to Coal yard(Truck) | nos | 0 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 23
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-23 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 107600 | 3878175 | 13167275
2 | Auxiliary power consumption | kWhr | 16876 | 417436 | 1475920
3 | Net Power Exported | kWhr | 90724 | 3460739 | 11691355
4 | Auxiliary power consumption | ( % ) | 15.684 | 10.7637 | 11.209
5 | Average Power Generation | MWhr | 4.4833 | 7.0257 | 6.5881
6 | Plant Running Hours | Hrs | 24 | 552 | 1998.66
6 | PLF | ( % ) | 44.8333 | 70.2568 | 65.8805
7 | Feed Water consumption | MT | 541 | 17952 | 61640
8 | Boiler Steam Generation | MT | 525 | 17335 | 59724
9 | Bleed steam | MT | 29 | 1265 | 3710
10 | Turbine steam consumption | MT | 473 | 16199 | 54813
11 | Condensate Generation | MT | 377 | 12872 | 44078
12 | Auxilairy steam consumption | MT | 18 | 409 | 1490
13 | Specific steam consumption | Kg/Kwhr | 4.3959 | 4.177 | 4.1628
14 | Specific fuel consumption | Kg/Kwhr | 0.87361 | 0.85298 | 0.87186
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2961.7937 | 2813.8434 | 2804.5901
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4209.8585 | 3856.7093 | 3913.573
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 94 | 3308 | 11480
2 | GCV ( ADB ) | Kcal/kg | 4799
WTP Report
1 | DM water Generation | m3 | 13 | 350 | 1305
2 | DM water Consumption | m3 | 12 | 355 | 1322
3 | CT Makeup Water Consumption | m3 | 18 | 441 | 1577
4 | Fly ash combustible/ GCV | % / kcal/kg | 12.57 | 1012
5 | Fly ash to cement mill | MT | 28 | 503 | 1874
6 | Fly ash to Coal yard(Truck) | nos | 0 | 57 | 212
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 24
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-24 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 160800 | 4038975 | 13328075
2 | Auxiliary power consumption | kWhr | 18489 | 435925 | 1494409
3 | Net Power Exported | kWhr | 142311 | 3603050 | 11833666
4 | Auxiliary power consumption | ( % ) | 11.4981 | 10.793 | 11.2125
5 | Average Power Generation | MWhr | 6.7 | 7.0121 | 6.5894
6 | Plant Running Hours | Hrs | 24 | 576 | 2022.66
6 | PLF | ( % ) | 67 | 70.1211 | 65.8938
7 | Feed Water consumption | MT | 747 | 18699 | 62387
8 | Boiler Steam Generation | MT | 718 | 18053 | 60442
9 | Bleed steam | MT | 53 | 1318 | 3763
10 | Turbine steam consumption | MT | 678 | 16877 | 55491
11 | Condensate Generation | MT | 533 | 13405 | 44611
12 | Auxilairy steam consumption | MT | 17 | 426 | 1507
13 | Specific steam consumption | Kg/Kwhr | 4.2164 | 4.1785 | 4.1635
14 | Specific fuel consumption | Kg/Kwhr | 0.8209 | 0.8517 | 0.87124
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2840.2612 | 2814.8951 | 2805.0205
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3852.6438 | 3856.5474 | 3912.8379
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 132 | 3440 | 11612
2 | GCV ( ADB ) | Kcal/kg | 4693
WTP Report
1 | DM water Generation | m3 | 15 | 365 | 1320
2 | DM water Consumption | m3 | 14 | 369 | 1336
3 | CT Makeup Water Consumption | m3 | 53 | 494 | 1630
4 | Fly ash combustible/ GCV | % / kcal/kg | 11.7 | 951
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 523 | 1894
6 | Fly ash to Coal yard(Truck) | nos | 2 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 25
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-25 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176200 | 4215175 | 13504275
2 | Auxiliary power consumption | kWhr | 18271 | 454196 | 1512680
3 | Net Power Exported | kWhr | 157929 | 3760979 | 11991595
4 | Auxiliary power consumption | ( % ) | 10.3695 | 10.7753 | 11.2015
5 | Average Power Generation | MWhr | 7.3417 | 7.0253 | 6.5982
6 | Plant Running Hours | Hrs | 24 | 600 | 2046.66
6 | PLF | ( % ) | 73.4167 | 70.2529 | 65.982
7 | Feed Water consumption | MT | 802 | 19501 | 63189
8 | Boiler Steam Generation | MT | 788 | 18841 | 61230
9 | Bleed steam | MT | 61 | 1379 | 3824
10 | Turbine steam consumption | MT | 738 | 17615 | 56229
11 | Condensate Generation | MT | 576 | 13981 | 45187
12 | Auxilairy steam consumption | MT | 19 | 445 | 1526
13 | Specific steam consumption | Kg/Kwhr | 4.1884 | 4.1789 | 4.1638
14 | Specific fuel consumption | Kg/Kwhr | 0.83995 | 0.85121 | 0.87084
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2821.0216 | 2815.1512 | 2805.2292
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3858.6979 | 3856.6373 | 3912.1315
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 148 | 3588 | 11760
2 | GCV ( ADB ) | Kcal/kg | 4593
WTP Report
1 | DM water Generation | m3 | 13 | 378 | 1333
2 | DM water Consumption | m3 | 13 | 382 | 1349
3 | CT Makeup Water Consumption | m3 | 59 | 553 | 1689
4 | Fly ash combustible/ GCV | % / kcal/kg | 16 | 1115
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 570 | 1941
6 | Fly ash to Coalyard(Truck) | nos | 0 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 26
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-26 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 170200 | 4385375 | 13674475
2 | Auxiliary power consumption | kWhr | 18058 | 472254 | 1530738
3 | Net Power Exported | kWhr | 152142 | 3913121 | 12143737
4 | Auxiliary power consumption | ( % ) | 10.6099 | 10.7688 | 11.1941
5 | Average Power Generation | MWhr | 7.0917 | 7.0278 | 6.6039
6 | Plant Running Hours | Hrs | 24 | 624 | 2070.66
6 | PLF | ( % ) | 70.9167 | 70.2784 | 66.0392
7 | Feed Water consumption | MT | 778 | 20279 | 63967
8 | Boiler Steam Generation | MT | 758 | 19599 | 61988
9 | Bleed steam | MT | 60 | 1439 | 3884
10 | Turbine steam consumption | MT | 709 | 18324 | 56938
11 | Condensate Generation | MT | 555 | 14536 | 45742
12 | Auxilairy steam consumption | MT | 17 | 462 | 1543
13 | Specific steam consumption | Kg/Kwhr | 4.1657 | 4.1784 | 4.1638
14 | Specific fuel consumption | Kg/Kwhr | 0.82256 | 0.8501 | 0.87023
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.7991 | 2814.7882 | 2805.2363
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3842.6436 | 3856.0942 | 3911.2666
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 140 | 3728 | 11900
2 | GCV ( ADB ) | Kcal/kg | 4664
WTP Report
1 | DM water Generation | m3 | 11 | 389 | 1344
2 | DM water Consumption | m3 | 13 | 395 | 1362
3 | CT Makeup Water Consumption | m3 | 18 | 571 | 1707
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1189
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 46 | 616 | 1987
6 | Fly ash to Coalyard(Truck) | nos | 0 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 27
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-27 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 168600 | 4553975 | 13843075
2 | Auxiliary power consumption | kWhr | 18014 | 490268 | 1548752
3 | Net Power Exported | kWhr | 150586 | 4063707 | 12294323
4 | Auxiliary power consumption | ( % ) | 10.6845 | 10.7657 | 11.1879
5 | Average Power Generation | MWhr | 7.025 | 7.0277 | 6.6087
6 | Plant Running Hours | Hrs | 24 | 648 | 2094.66
6 | PLF | ( % ) | 70.25 | 70.2774 | 66.0875
7 | Feed Water consumption | MT | 774 | 21053 | 64741
8 | Boiler Steam Generation | MT | 753 | 20352 | 62741
9 | Bleed steam | MT | 66 | 1505 | 3950
10 | Turbine steam consumption | MT | 703 | 19027 | 57641
11 | Condensate Generation | MT | 549 | 15085 | 46291
12 | Auxilairy steam consumption | MT | 18 | 480 | 1561
13 | Specific steam consumption | Kg/Kwhr | 4.1696 | 4.1781 | 4.1639
14 | Specific fuel consumption | Kg/Kwhr | 0.84816 | 0.85003 | 0.86997
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2809.0095 | 2814.5743 | 2805.2823
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3853.5222 | 3855.999 | 3910.5634
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 143 | 3871 | 12043
2 | GCV ( ADB ) | Kcal/kg | 4532 | 0
WTP Report
1 | DM water Generation | m3 | 18 | 407 | 1362
2 | DM water Consumption | m3 | 16 | 411 | 1378
3 | CT Makeup Water Consumption | m3 | 20 | 591 | 1727
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1325
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 48 | 664 | 2035
6 | Fly ash to Coalyard(Truck) | nos | 0 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 28
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-28 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 170400 | 4724375 | 14013475
2 | Auxiliary power consumption | kWhr | 18125 | 508393 | 1566877
3 | Net Power Exported | kWhr | 152275 | 4215982 | 12446598
4 | Auxiliary power consumption | ( % ) | 10.6367 | 10.7611 | 11.1812
5 | Average Power Generation | MWhr | 7.1 | 7.0303 | 6.6143
6 | Plant Running Hours | Hrs | 24 | 672 | 2118.66
6 | PLF | ( % ) | 71 | 70.3032 | 66.1431
7 | Feed Water consumption | MT | 780 | 21833 | 65521
8 | Boiler Steam Generation | MT | 757 | 21109 | 63498
9 | Bleed steam | MT | 57 | 1562 | 4007
10 | Turbine steam consumption | MT | 713 | 19740 | 58354
11 | Condensate Generation | MT | 559 | 15644 | 46850
12 | Auxilairy steam consumption | MT | 17 | 497 | 1578
13 | Specific steam consumption | Kg/Kwhr | 4.1843 | 4.1783 | 4.1641
14 | Specific fuel consumption | Kg/Kwhr | 0.85094 | 0.85006 | 0.86973
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2819.0082 | 2814.7342 | 2805.4492
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3833.07 | 3855.172 | 3909.6211
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 145 | 4016 | 12188
2 | GCV ( ADB ) | Kcal/kg | 4498
WTP Report
1 | DM water Generation | m3 | 18 | 425 | 1380
2 | DM water Consumption | m3 | 17 | 428 | 1395
3 | CT Makeup Water Consumption | m3 | 19 | 610 | 1746
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1187
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 51 | 715 | 2086
6 | Fly ash to Coalyard(Truck) | nos | 0 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 29
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-29 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 175890 | 4900265 | 14189365
2 | Auxiliary power consumption | kWhr | 18202 | 526595 | 1585079
3 | Net Power Exported | kWhr | 157688 | 4373670 | 12604286
4 | Auxiliary power consumption | ( % ) | 10.3485 | 10.7463 | 11.1709
5 | Average Power Generation | MWhr | 7.8173 | 7.0558 | 6.627
6 | Plant Running Hours | Hrs | 22.5 | 694.5 | 2141.16
6 | PLF | ( % ) | 78.1733 | 70.5582 | 66.2695
7 | Feed Water consumption | MT | 804 | 22637 | 66325
8 | Boiler Steam Generation | MT | 778 | 21887 | 64276
9 | Bleed steam | MT | 60 | 1622 | 4067
10 | Turbine steam consumption | MT | 729 | 20469 | 59083
11 | Condensate Generation | MT | 572 | 16216 | 47422
12 | Auxilairy steam consumption | MT | 19 | 516 | 1597
13 | Specific steam consumption | Kg/Kwhr | 4.1446 | 4.1771 | 4.1639
14 | Specific fuel consumption | Kg/Kwhr | 0.85281 | 0.85016 | 0.86952
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2791.5572 | 2813.9023 | 2805.277
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3816.4441 | 3853.7819 | 3908.466
17 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL Report
1 | Coal Consumption | MT | 150 | 4166 | 12338
2 | GCV ( ADB ) | Kcal/kg | 4451
WTP Report
1 | DM water Generation | m3 | 12 | 437 | 1392
2 | DM water Consumption | m3 | 13 | 441 | 1408
3 | CT Makeup Water Consumption | m3 | 18 | 628 | 1764
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1423
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 52 | 767 | 2138
6 | Fly ash to Coalyard(Truck) | nos | 0 | 59 | 214
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 30
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 130600 | 5030865 | 14319965
2 | Auxiliary power consumption | kWhr | 17516 | 544111 | 1602595
3 | Net Power Exported | kWhr | 113084 | 4486754 | 12717370
4 | Auxiliary power consumption | ( % ) | 13.4119 | 10.8155 | 11.1913
5 | Average Power Generation | MWhr | 5.8044 | 7.0165 | 6.6184
6 | Plant Running Hours | Hrs | 22.5 | 717 | 2163.66
6 | PLF | ( % ) | 58.0444 | 70.1655 | 66.184
7 | Feed Water consumption | MT | 675 | 23312 | 67000
8 | Boiler Steam Generation | MT | 637 | 22524 | 64913
9 | Bleed steam | MT | 21 | 1643 | 4088
10 | Turbine steam consumption | MT | 543 | 21012 | 59626
11 | Condensate Generation | MT | 462 | 16678 | 47884
12 | Auxilairy steam consumption | MT | 18 | 534 | 1615
13 | Specific steam consumption | Kg/Kwhr | 4.1577 | 4.1766 | 4.1638
14 | Specific fuel consumption | Kg/Kwhr | 0.93415 | 0.85234 | 0.87011
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2807.343 | 2813.732 | 2805.2958
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4208.3971 | 3862.9876 | 3911.2015
17 | DG Power Generation | kWhr | 1468 | 1468 | 1468
FUEL Report
1 | Coal Consumption | MT | 122 | 4288 | 12460
2 | GCV ( ADB ) | Kcal/kg | 4509
WTP Report
1 | DM water Generation | m3 | 41 | 478 | 1433
2 | DM water Consumption | m3 | 40 | 481 | 1448
3 | CT Makeup Water Consumption | m3 | 18 | 646 | 1782
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.62 | 1421
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 787 | 2158
6 | Fly ash to Coalyard(Truck) | nos | 2 | 61 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0