## APR-2026
LAKE CEMENT LIMITED
POWER PLANT REPORT |  |  |  | DATE | 2026-04-21
SN | Description | UNIT | ON DATE | MONTH TO DATE | YEAR TO DATE(APR 2026-MAR 2027)
1 | Gross Power Generation | kWhr | 139400 | 3085200 | 3085200
2 | Auxiliary Power Consumption | kWhr | 17157 | 360034 | 360034
3 | Net Power Exported | kWhr | 122243 | 2725166 | 2725166
4 | Auxiliary power Consumption | ( % ) | 12.3077 | 11.6697 | 11.6697
5 | Average Power Generation | MWhr | 5.8083 | 6.3395 | 6.3395
6 | Plant Running Hours | Hrs | 24 | 486.66 | 486.66
7 | PLF | ( % ) | 58.0833 | 63.3954 | 63.3954
8 | Feed Water Consumption | MT | 660 | 14512 | 14512
9 | Boiler Steam Generation | MT | 644 | 14122 | 14122
10 | Bleed Steam | MT | 41 | 839 | 839
11 | Turbine Steam Consumption | MT | 579 | 12899 | 12899
12 | Condensate Generation | MT | 464 | 10490 | 10490
13 | Auxilairy Steam Consumption | MT | 19 | 367 | 367
14 | Specific Steam Consumption | Kg/Kwhr | 4.1535 | 4.1809 | 4.1809
15 | Specific Fuel Consumption | Kg/Kwhr | 0.94692 | 0.88357 | 0.88357
16 | Heat Rate (TG) 2880 | Kcal/Kwh | 2798.5438 | 2817.3723 | 2817.3723
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3986.0575 | 3949.4202 | 3949.4202
18 | DG Power Generation | kWhr | 0 | 0 | 0
FUEL REPORT
1 | Coal Consumption | MT | 132 | 2726 | 2726
2 | GCV ( ADB ) | Kcal/kg | 4179
WTP REPORT
1 | DM Water Generation | m3 | 14 | 356 | 356
2 | DM Water Consumption | m3 | 15 | 371 | 371
3 | CT Makeup Water Consumption | m3 | 18 | 383 | 383
4 | Fly Ash Combustible / GCV | % / kcal/kg | 18 | 1286
FLY ASH DISPOSAL REPORT
1 | Fly Ash to Cement mill | Ton | 18 | 430 | 430
2 | Fly Ash to Coalyard (Truck) | nos | 3 | 47 | 47
3 | Fly Ash to Dumpyard (Truck) | nos | 0 | 0 | 0
Coal consumed:-
Market insight : 0TONS.
connect:- 0 TONS..
STAMICO:- 66TON
Ruvuma : 66 TONS
MCHEKANAI : 0 TON