## 0
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 180300 | 5406400 | 19726365
2 | Auxiliary power consumption | kWhr | 17840 | 550950 | 2153545
3 | Net Power Exported | kWhr | 162460 | 4855450 | 17572820
4 | Auxiliary power consumption | ( % ) | 9.8946 | 10.1907 | 10.9171
5 | Average Power Generation | MWhr | 7.5125 | 7.2667 | 6.7843
6 | Plant Running Hours | Hrs | 24 | 744 | 2907.66
6 | PLF | ( % ) | 75.125 | 72.6667 | 67.8427
7 | Feed Water consumption | MT | 824 | 24773 | 91773
8 | Boiler Steam Generation | MT | 796 | 24075 | 88988
9 | Bleed steam | MT | 57 | 1692 | 5780
10 | Turbine steam consumption | MT | 751 | 22547 | 82173
11 | Condensate Generation | MT | 593 | 17729 | 65613
12 | Auxilairy steam consumption | MT | 0 | 534 | 2149
13 | Specific steam consumption | Kg/Kwhr | 4.1653 | 4.1704 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.7543 | 0.81089 | 0.85388
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.2302 | 2808.9673 | 2806.3021
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3809.2353 | 3842.1877 | 3892.2869
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 136 | 4384 | 16844
2 | GCV ( ADB ) | Kcal/kg | 4768
WTP Report
1 | DM water Generation | m3 | 12 | 410 | 1843
2 | DM water Consumption | m3 | 12 | 409 | 1857
3 | CT Makeup Water Consumption | m3 | 17 | 651 | 2433
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1668
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 1 | 791 | 2949
6 | Fly ash to Coalyard(Truck) | nos | 32 | 93 | 309
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 1
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-01 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178900 | 178900 | 19905265
2 | Auxiliary power consumption | kWhr | 18109 | 18109 | 2171654
3 | Net Power Exported | kWhr | 160791 | 160791 | 17733611
4 | Auxiliary power consumption | ( % ) | 10.1224 | 10.1224 | 10.9099
5 | Average Power Generation | MWhr | 7.4542 | 7.4542 | 6.7898
6 | Plant Running Hours | Hrs | 24 | 24 | 2931.66
6 | PLF | ( % ) | 74.5417 | 74.5417 | 67.8976
7 | Feed Water consumption | MT | 808 | 808 | 92581
8 | Boiler Steam Generation | MT | 790 | 790 | 89778
9 | Bleed steam | MT | 51 | 51 | 5831
10 | Turbine steam consumption | MT | 745 | 745 | 82918
11 | Condensate Generation | MT | 586 | 586 | 66199
12 | Auxilairy steam consumption | MT | 18 | 18 | 2167
13 | Specific steam consumption | Kg/Kwhr | 4.1643 | 4.1643 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.76579 | 0.76579 | 0.85309
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.1146 | 2805.1146 | 2806.2914
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3810.1074 | 3810.1074 | 3891.5483
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 137 | 137 | 16981
2 | GCV ( ADB ) | Kcal/kg | 4780
WTP Report
1 | DM water Generation | m2 | 14 | 14 | 1857
2 | DM water Consumption | m3 | 15 | 15 | 1872
3 | CT Makeup Water Consumption | m3 | 21 | 21 | 2454
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1653
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 44 | 44 | 2993
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 309
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 2
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-02 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 185651 | 364551 | 20090916
2 | Auxiliary power consumption | kWhr | 18409 | 36518 | 2190063
3 | Net Power Exported | kWhr | 167242 | 328033 | 17900853
4 | Auxiliary power consumption | ( % ) | 9.9159 | 10.0173 | 10.9008
5 | Average Power Generation | MWhr | 7.7355 | 7.5948 | 6.7974
6 | Plant Running Hours | Hrs | 24 | 48 | 2955.66
7 | PLF | ( % ) | 77.3546 | 75.9481 | 67.9744
8 | Feed Water consumption | MT | 826 | 1634 | 93407
9 | Boiler Steam Generation | MT | 820 | 1610 | 90598
10 | Bleed steam | MT | 58 | 109 | 5889
11 | Turbine steam consumption | MT | 761 | 1506 | 83679
12 | Condensate Generation | MT | 597 | 1183 | 66796
13 | Auxilairy steam consumption | MT | 17 | 35 | 2184
14 | Specific steam consumption | Kg/Kwhr | 4.0991 | 4.1311 | 4.165
15 | Specific fuel consumption | Kg/Kwhr | 0.74333 | 0.75435 | 0.85208
16 | Heat Rate(TG)2880 | Kcal/Kwh | 2760.6261 | 2782.4584 | 2805.8694
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3810.9831 | 3810.5533 | 3890.8038
18 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 138 | 275 | 17119
2 | GCV ( ADB ) | Kcal/kg | 4604
WTP Report
1 | DM water Generation | m3 | 11 | 25 | 1868
2 | DM water Consumption | m3 | 12 | 27 | 1884
3 | CT Makeup Water Consumption | m3 | 18 | 39 | 2472
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1614
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 91 | 3040
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 309
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 3
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-03 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176600 | 541151 | 20267516
2 | Auxiliary power consumption | kWhr | 17918 | 54436 | 2207981
3 | Net Power Exported | kWhr | 158682 | 486715 | 18059535
4 | Auxiliary power consumption | ( % ) | 10.1461 | 10.0593 | 10.8942
5 | Average Power Generation | MWhr | 7.3583 | 7.516 | 6.802
6 | Plant Running Hours | Hrs | 24 | 72 | 2979.66
6 | PLF | ( % ) | 73.5833 | 75.1599 | 68.0196
7 | Feed Water consumption | MT | 818 | 2452 | 94225
8 | Boiler Steam Generation | MT | 788 | 2398 | 91386
9 | Bleed steam | MT | 60 | 169 | 5949
10 | Turbine steam consumption | MT | 746 | 2252 | 84425
11 | Condensate Generation | MT | 589 | 1772 | 67385
12 | Auxilairy steam consumption | MT | 18 | 53 | 2202
13 | Specific steam consumption | Kg/Kwhr | 4.2242 | 4.1615 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.74745 | 0.7521 | 0.85116
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2846.1382 | 2803.2398 | 2806.2203
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3849.9579 | 3823.4127 | 3890.4479
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 132 | 407 | 17251
2 | GCV ( ADB ) | Kcal/kg | 4636
WTP Report
1 | DM water Generation | m3 | 18 | 43 | 1886
2 | DM water Consumption | m3 | 19 | 46 | 1903
3 | CT Makeup Water Consumption | m3 | 18 | 57 | 2490
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1612
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 46 | 137 | 3086
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 309
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 4
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-04 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 182500 | 723651 | 20450016
2 | Auxiliary power consumption | kWhr | 18031 | 72467 | 2226012
3 | Net Power Exported | kWhr | 164469 | 651184 | 18224004
4 | Auxiliary power consumption | ( % ) | 9.88 | 10.0141 | 10.8851
5 | Average Power Generation | MWhr | 7.6042 | 7.538 | 6.8084
6 | Plant Running Hours | Hrs | 24 | 96 | 3003.66
6 | PLF | ( % ) | 76.0417 | 75.3803 | 68.0837
7 | Feed Water consumption | MT | 831 | 3283 | 95056
8 | Boiler Steam Generation | MT | 807 | 3205 | 92193
9 | Bleed steam | MT | 61 | 230 | 6010
10 | Turbine steam consumption | MT | 762 | 3014 | 85187
11 | Condensate Generation | MT | 598 | 2370 | 67983
12 | Auxilairy steam consumption | MT | 18 | 71 | 2220
13 | Specific steam consumption | Kg/Kwhr | 4.1753 | 4.165 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.75068 | 0.75174 | 0.85027
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.4712 | 2805.5679 | 2806.2761
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3815.3214 | 3821.3721 | 3889.7775
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 137 | 544 | 17388
2 | GCV ( ADB ) | Kcal/kg | 4623
WTP Report
1 | DM water Generation | m3 | 17 | 60 | 1903
2 | DM water Consumption | m3 | 15 | 61 | 1918
3 | CT Makeup Water Consumption | m3 | 23 | 80 | 2513
4 | Fly ash combustible/ GCV | % / kcal/kg | 19.78 | 1518
5 | Fly ash to cement mill | MT | 25 | 162 | 3111
6 | Fly ash to Coal yard(Truck) | nos | 2 | 2 | 311
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 5
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-05 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 183200 | 906851 | 20633216
2 | Auxiliary power consumption | kWhr | 18232 | 90699 | 2244244
3 | Net Power Exported | kWhr | 164968 | 816152 | 18388972
4 | Auxiliary power consumption | ( % ) | 9.952 | 10.0015 | 10.8769
5 | Average Power Generation | MWhr | 7.6333 | 7.5571 | 6.8149
6 | Plant Running Hours | Hrs | 24 | 120 | 3027.66
6 | PLF | ( % ) | 76.3333 | 75.5709 | 68.1491
7 | Feed Water consumption | MT | 828 | 4111 | 95884
8 | Boiler Steam Generation | MT | 810 | 4015 | 93003
9 | Bleed steam | MT | 62 | 292 | 6072
10 | Turbine steam consumption | MT | 761 | 3775 | 85948
11 | Condensate Generation | MT | 596 | 2966 | 68579
12 | Auxilairy steam consumption | MT | 18 | 89 | 2238
13 | Specific steam consumption | Kg/Kwhr | 4.1539 | 4.1628 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.75328 | 0.75205 | 0.84941
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2797.7238 | 2803.9832 | 2806.2002
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3814.8724 | 3820.059 | 3889.1124
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 138 | 682 | 17526
2 | GCV ( ADB ) | Kcal/kg | 4729
WTP Report
1 | DM water Generation | m3 | 12 | 72 | 1915
2 | DM water Consumption | m3 | 13 | 74 | 1931
3 | CT Makeup Water Consumption | m3 | 23 | 103 | 2536
4 | Fly ash combustible/ GCV | % / kcal/kg | 21.64 | 1572
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 15 | 177 | 3126
6 | Fly ash to Coal yard(Truck) | nos | 3 | 5 | 314
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 6
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-06 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 167800 | 1074651 | 20801016
2 | Auxiliary power consumption | kWhr | 18139 | 108838 | 2262383
3 | Net Power Exported | kWhr | 149661 | 965813 | 18538633
4 | Auxiliary power consumption | ( % ) | 10.8099 | 10.1278 | 10.8763
5 | Average Power Generation | MWhr | 6.9917 | 7.4629 | 6.8163
6 | Plant Running Hours | Hrs | 24 | 144 | 3051.66
6 | PLF | ( % ) | 69.9167 | 74.6285 | 68.163
7 | Feed Water consumption | MT | 768 | 4879 | 96652
8 | Boiler Steam Generation | MT | 748 | 4763 | 93751
9 | Bleed steam | MT | 54 | 346 | 6126
10 | Turbine steam consumption | MT | 703 | 4478 | 86651
11 | Condensate Generation | MT | 551 | 3517 | 69130
12 | Auxilairy steam consumption | MT | 18 | 107 | 2256
13 | Specific steam consumption | Kg/Kwhr | 4.1895 | 4.1669 | 4.1657
14 | Specific fuel consumption | Kg/Kwhr | 0.73302 | 0.74908 | 0.84847
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2821.8653 | 2806.7754 | 2806.3265
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3846.1844 | 3824.1384 | 3888.7661
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 123 | 805 | 17649
2 | GCV ( ADB ) | Kcal/kg | 4601
WTP Report
1 | DM water Generation | m3 | 13 | 85 | 1928
2 | DM water Consumption | m3 | 13 | 87 | 1944
3 | CT Makeup Water Consumption | m3 | 54 | 157 | 2590
4 | Fly ash combustible/ GCV | % / kcal/kg | 17.28 | 1396
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 177 | 3126
6 | Fly ash to Coal yard(Truck) | nos | 4 | 9 | 318
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 7
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-07 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 190900 | 1265551 | 20991916
2 | Auxiliary power consumption | kWhr | 18474 | 127312 | 2280857
3 | Net Power Exported | kWhr | 172426 | 1138239 | 18711059
4 | Auxiliary power consumption | ( % ) | 9.6773 | 10.0598 | 10.8654
5 | Average Power Generation | MWhr | 7.9542 | 7.533 | 6.8252
6 | Plant Running Hours | Hrs | 24 | 168 | 3075.66
6 | PLF | ( % ) | 79.5417 | 75.3304 | 68.2517
7 | Feed Water consumption | MT | 861 | 5740 | 97513
8 | Boiler Steam Generation | MT | 840 | 5603 | 94591
9 | Bleed steam | MT | 64 | 410 | 6190
10 | Turbine steam consumption | MT | 795 | 5273 | 87446
11 | Condensate Generation | MT | 621 | 4138 | 69751
12 | Auxilairy steam consumption | MT | 18 | 125 | 2274
13 | Specific steam consumption | Kg/Kwhr | 4.1645 | 4.1666 | 4.1657
14 | Specific fuel consumption | Kg/Kwhr | 0.75956 | 0.75066 | 0.84766
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2804.2693 | 2806.3974 | 2806.3078
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3796.591 | 3819.983 | 3887.9279
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 145 | 950 | 17794
2 | GCV ( ADB ) | Kcal/kg | 4646
1 | DM water Generation | m3 | 11 | 96 | 1939
2 | DM water Consumption | m3 | 10 | 97 | 1954
3 | CT Makeup Water Consumption | m3 | 18 | 175 | 2608
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1387
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 177 | 3126
6 | Fly ash to Coal yard(Truck) | nos | 5 | 14 | 323
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 8
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-08 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 180000 | 1445551 | 21171916
2 | Auxiliary power consumption | kWhr | 18256 | 145568 | 2299113
3 | Net Power Exported | kWhr | 161744 | 1299983 | 18872803
4 | Auxiliary power consumption | ( % ) | 10.1422 | 10.0701 | 10.8593
5 | Average Power Generation | MWhr | 7.5 | 7.5289 | 6.8304
6 | Plant Running Hours | Hrs | 24 | 192 | 3099.66
6 | PLF | ( % ) | 75 | 75.2891 | 68.304
7 | Feed Water consumption | MT | 819 | 6559 | 98332
8 | Boiler Steam Generation | MT | 799 | 6402 | 95390
9 | Bleed steam | MT | 60 | 470 | 6250
10 | Turbine steam consumption | MT | 751 | 6024 | 88197
11 | Condensate Generation | MT | 589 | 4727 | 70340
12 | Auxilairy steam consumption | MT | 17 | 142 | 2291
13 | Specific steam consumption | Kg/Kwhr | 4.1722 | 4.1673 | 4.1658
14 | Specific fuel consumption | Kg/Kwhr | 0.75556 | 0.75127 | 0.84688
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2810.4056 | 2806.8965 | 2806.3427
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3829.9644 | 3821.2259 | 3887.4351
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 136 | 1086 | 17930
2 | GCV ( ADB ) | Kcal/kg | 4244
WTP Report
1 | DM water Generation | m3 | 13 | 109 | 1952
2 | DM water Consumption | m3 | 15 | 112 | 1969
3 | CT Makeup Water Consumption | m3 | 18 | 193 | 2626
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1354
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 40 | 217 | 3166
6 | Fly ash to Coal yard(Truck) | nos | 1 | 15 | 324
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 9
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-09 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 179600 | 1625151 | 21351516
2 | Auxiliary power consumption | kWhr | 18251 | 163819 | 2317364
3 | Net Power Exported | kWhr | 161349 | 1461332 | 19034152
4 | Auxiliary power consumption | ( % ) | 10.162 | 10.0802 | 10.8534
5 | Average Power Generation | MWhr | 7.4833 | 7.5238 | 6.8354
6 | Plant Running Hours | Hrs | 24 | 216 | 3123.66
6 | PLF | ( % ) | 74.8333 | 75.2385 | 68.3542
7 | Feed Water consumption | MT | 809 | 7368 | 99141
8 | Boiler Steam Generation | MT | 792 | 7194 | 96182
9 | Bleed steam | MT | 59 | 529 | 6309
10 | Turbine steam consumption | MT | 743 | 6767 | 88940
11 | Condensate Generation | MT | 582 | 5309 | 70922
12 | Auxilairy steam consumption | MT | 18 | 160 | 2309
13 | Specific steam consumption | Kg/Kwhr | 4.137 | 4.1639 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.75167 | 0.75131 | 0.84608
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2786.353 | 2804.6262 | 2806.1745
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3804.8655 | 3819.4179 | 3886.7405
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 135 | 1221 | 18065
2 | GCV ( ADB ) | Kcal/kg | 4132
WTP Report
1 | DM water Generation | m3 | 13 | 122 | 1965
2 | DM water Consumption | m3 | 13 | 125 | 1982
3 | CT Makeup Water Consumption | m3 | 19 | 212 | 2645
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1313
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 54 | 271 | 3220
6 | Fly ash to Coal yard(Truck) | nos | 0 | 15 | 324
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 10
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-10 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 164700 | 1789851 | 21516216
2 | Auxiliary power consumption | kWhr | 18095 | 181914 | 2335459
3 | Net Power Exported | kWhr | 146605 | 1607937 | 19180757
4 | Auxiliary power consumption | ( % ) | 10.9866 | 10.1636 | 10.8544
5 | Average Power Generation | MWhr | 6.8625 | 7.4577 | 6.8356
6 | Plant Running Hours | Hrs | 24 | 240 | 3147.66
6 | PLF | ( % ) | 68.625 | 74.5771 | 68.3562
7 | Feed Water consumption | MT | 769 | 8137 | 99910
8 | Boiler Steam Generation | MT | 736 | 7930 | 96918
9 | Bleed steam | MT | 50 | 579 | 6359
10 | Turbine steam consumption | MT | 687 | 7454 | 89627
11 | Condensate Generation | MT | 550 | 5859 | 71472
12 | Auxilairy steam consumption | MT | 17 | 177 | 2326
13 | Specific steam consumption | Kg/Kwhr | 4.1712 | 4.1646 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.75896 | 0.75202 | 0.84541
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2810.8743 | 2805.2011 | 2806.2105
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3855.7128 | 3822.7577 | 3886.503
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 125 | 1346 | 18190
2 | GCV ( ADB ) | Kcal/kg | 4131
WTP Report
1 | DM water Generation | m3 | 22 | 144 | 1987
2 | DM water Consumption | m3 | 20 | 145 | 2002
3 | CT Makeup Water Consumption | m3 | 19 | 231 | 2664
4 | Fly ash combustible/ GCV | % / kcal/kg | 16 | 1287
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 318 | 3267
6 | Fly ash to Coal yard(Truck) | nos | 0 | 15 | 324
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 11
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-11 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 138500 | 1928351 | 21654716
2 | Auxiliary power consumption | kWhr | 17702 | 199616 | 2353161
3 | Net Power Exported | kWhr | 120798 | 1728735 | 19301555
4 | Auxiliary power consumption | ( % ) | 12.7812 | 10.3516 | 10.8667
5 | Average Power Generation | MWhr | 5.7708 | 7.3044 | 6.8276
6 | Plant Running Hours | Hrs | 24 | 264 | 3171.66
6 | PLF | ( % ) | 57.7083 | 73.0436 | 68.2757
7 | Feed Water consumption | MT | 674 | 8811 | 100584
8 | Boiler Steam Generation | MT | 654 | 8584 | 97572
9 | Bleed steam | MT | 34 | 613 | 6393
10 | Turbine steam consumption | MT | 582 | 8036 | 90209
11 | Condensate Generation | MT | 475 | 6334 | 71947
12 | Auxilairy steam consumption | MT | 18 | 195 | 2344
13 | Specific steam consumption | Kg/Kwhr | 4.2022 | 4.1673 | 4.1658
14 | Specific fuel consumption | Kg/Kwhr | 0.75812 | 0.75246 | 0.84485
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2831.5235 | 2807.0917 | 2806.3724
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4074.2572 | 3840.8211 | 3887.7039
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 105 | 1451 | 18295
2 | GCV ( ADB ) | Kcal/kg | 4041
WTP Report
1 | DM water Generation | m3 | 15 | 159 | 2002
2 | DM water Consumption | m3 | 16 | 161 | 2018
3 | CT Makeup Water Consumption | m3 | 18 | 249 | 2682
4 | Fly ash combustible/ GCV | % / kcal/kg | 15.8 | 1299
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 338 | 3287
6 | Fly ash to Coal yard(Truck) | nos | 2 | 17 | 326
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 12
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-12 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 163400 | 2091751 | 21818116
2 | Auxiliary power consumption | kWhr | 18035 | 217651 | 2371196
3 | Net Power Exported | kWhr | 145365 | 1874100 | 19446920
4 | Auxiliary power consumption | ( % ) | 11.0373 | 10.4052 | 10.868
5 | Average Power Generation | MWhr | 6.8083 | 7.263 | 6.8274
6 | Plant Running Hours | Hrs | 24 | 288 | 3195.66
6 | PLF | ( % ) | 68.0833 | 72.6302 | 68.2742
7 | Feed Water consumption | MT | 754 | 9565 | 101338
8 | Boiler Steam Generation | MT | 730 | 9314 | 98302
9 | Bleed steam | MT | 57 | 670 | 6450
10 | Turbine steam consumption | MT | 684 | 8720 | 90893
11 | Condensate Generation | MT | 537 | 6871 | 72484
12 | Auxilairy steam consumption | MT | 18 | 213 | 2362
13 | Specific steam consumption | Kg/Kwhr | 4.186 | 4.1688 | 4.1659
14 | Specific fuel consumption | Kg/Kwhr | 0.75275 | 0.75248 | 0.84416
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2819.7797 | 2808.0828 | 2806.4728
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3854.7061 | 3841.9058 | 3887.4567
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 123 | 1574 | 18418
2 | GCV ( ADB ) | Kcal/kg | 4160
WTP Report
1 | DM water Generation | m3 | 15 | 174 | 2017
2 | DM water Consumption | m3 | 14 | 175 | 2032
3 | CT Makeup Water Consumption | m3 | 18 | 267 | 2700
4 | Fly ash combustible/ GCV | % / kcal/kg | 15.7 | 1277
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 46 | 384 | 3333
6 | Fly ash to Coal yard(Truck) | nos | 0 | 17 | 326
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 13
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-13 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 161400 | 2253151 | 21979516
2 | Auxiliary power consumption | kWhr | 17860 | 235511 | 2389056
3 | Net Power Exported | kWhr | 143540 | 2017640 | 19590460
4 | Auxiliary power consumption | ( % ) | 11.0657 | 10.4525 | 10.8695
5 | Average Power Generation | MWhr | 6.725 | 7.2216 | 6.8267
6 | Plant Running Hours | Hrs | 24 | 312 | 3219.66
6 | PLF | ( % ) | 67.25 | 72.2164 | 68.2666
7 | Feed Water consumption | MT | 751 | 10316 | 102089
8 | Boiler Steam Generation | MT | 717 | 10031 | 99019
9 | Bleed steam | MT | 57 | 727 | 6507
10 | Turbine steam consumption | MT | 679 | 9399 | 91572
11 | Condensate Generation | MT | 535 | 7406 | 73019
12 | Auxilairy steam consumption | MT | 18 | 231 | 2380
13 | Specific steam consumption | Kg/Kwhr | 4.2069 | 4.1715 | 4.1662
14 | Specific fuel consumption | Kg/Kwhr | 0.75589 | 0.75272 | 0.84351
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2835.1735 | 2810.0234 | 2806.6836
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3832.9759 | 3841.2661 | 3887.0567
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 122 | 1696 | 18540
2 | GCV ( ADB ) | Kcal/kg | 4211
WTP Report
1 | DM water Generation | m3 | 21 | 195 | 2038
2 | DM water Consumption | m3 | 21 | 196 | 2053
3 | CT Makeup Water Consumption | m3 | 18 | 285 | 2718
4 | Fly ash combustible/ GCV | % / kcal/kg | 15.17 | 1170
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 15 | 399 | 3348
6 | Fly ash to Coal yard(Truck) | nos | 3 | 20 | 329
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 14
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-14 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 183700 | 2436851 | 22163216
2 | Auxiliary power consumption | kWhr | 18343 | 253854 | 2407399
3 | Net Power Exported | kWhr | 165357 | 2182997 | 19755817
4 | Auxiliary power consumption | ( % ) | 9.9853 | 10.4173 | 10.8621
5 | Average Power Generation | MWhr | 7.6542 | 7.2525 | 6.8328
6 | Plant Running Hours | Hrs | 24 | 336 | 3243.66
6 | PLF | ( % ) | 76.5417 | 72.5253 | 68.3278
7 | Feed Water consumption | MT | 833 | 11149 | 102922
8 | Boiler Steam Generation | MT | 816 | 10847 | 99835
9 | Bleed steam | MT | 68 | 795 | 6575
10 | Turbine steam consumption | MT | 767 | 10166 | 92339
11 | Condensate Generation | MT | 596 | 8002 | 73615
12 | Auxilairy steam consumption | MT | 17 | 248 | 2397
13 | Specific steam consumption | Kg/Kwhr | 4.1753 | 4.1718 | 4.1663
14 | Specific fuel consumption | Kg/Kwhr | 0.75122 | 0.75261 | 0.84275
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2811.6004 | 2810.1423 | 2806.7243
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3832.6703 | 3840.6181 | 3886.6059
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 138 | 1834 | 18678
2 | GCV ( ADB ) | Kcal/kg | 4230
WTP Report
1 | DM water Generation | m3 | 10 | 205 | 2048
2 | DM water Consumption | m3 | 10 | 206 | 2063
3 | CT Makeup Water Consumption | m3 | 18 | 303 | 2736
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1345
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 399 | 3348
6 | Fly ash to Coal yard(Truck) | nos | 4 | 24 | 333
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 15
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-15 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 180900 | 2617751 | 22344116
2 | Auxiliary power consumption | kWhr | 18333 | 272187 | 2425732
3 | Net Power Exported | kWhr | 162567 | 2345564 | 19918384
4 | Auxiliary power consumption | ( % ) | 10.1343 | 10.3977 | 10.8562
5 | Average Power Generation | MWhr | 7.5375 | 7.2715 | 6.838
6 | Plant Running Hours | Hrs | 24 | 360 | 3267.66
6 | PLF | ( % ) | 75.375 | 72.7153 | 68.3796
7 | Feed Water consumption | MT | 821 | 11970 | 103743
8 | Boiler Steam Generation | MT | 803 | 11650 | 100638
9 | Bleed steam | MT | 66 | 861 | 6641
10 | Turbine steam consumption | MT | 754 | 10920 | 93093
11 | Condensate Generation | MT | 585 | 8587 | 74200
12 | Auxilairy steam consumption | MT | 18 | 266 | 2415
13 | Specific steam consumption | Kg/Kwhr | 4.168 | 4.1715 | 4.1663
14 | Specific fuel consumption | Kg/Kwhr | 0.7518 | 0.75255 | 0.84201
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.921 | 2809.9197 | 2806.7259
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3829.9882 | 3839.8835 | 3886.1475
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 136 | 1970 | 18814
2 | GCV ( ADB ) | Kcal/kg | 4197
WTP Report
1 | DM water Generation | m3 | 11 | 216 | 2059
2 | DM water Consumption | m3 | 11 | 217 | 2074
3 | CT Makeup Water Consumption | m3 | 18 | 321 | 2754
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1287
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 399 | 3348
6 | Fly ash to Coal yard(Truck) | nos | 6 | 30 | 339
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 16
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-16 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 171500 | 2789251 | 22515616
2 | Auxiliary power consumption | kWhr | 17843 | 290030 | 2443575
3 | Net Power Exported | kWhr | 153657 | 2499221 | 20072041
4 | Auxiliary power consumption | ( % ) | 10.4041 | 10.3981 | 10.8528
5 | Average Power Generation | MWhr | 7.1458 | 7.2637 | 6.8402
6 | Plant Running Hours | Hrs | 24 | 384 | 3291.66
6 | PLF | ( % ) | 71.4583 | 72.6367 | 68.402
7 | Feed Water consumption | MT | 784 | 12754 | 104527
8 | Boiler Steam Generation | MT | 765 | 12415 | 101403
9 | Bleed steam | MT | 62 | 923 | 6703
10 | Turbine steam consumption | MT | 716 | 11636 | 93809
11 | Condensate Generation | MT | 559 | 9146 | 74759
12 | Auxilairy steam consumption | MT | 18 | 284 | 2433
13 | Specific steam consumption | Kg/Kwhr | 4.1749 | 4.1717 | 4.1664
14 | Specific fuel consumption | Kg/Kwhr | 0.75802 | 0.75289 | 0.84137
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812 | 2810.0476 | 2806.7661
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3848.7329 | 3840.4277 | 3885.8625
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 130 | 2100 | 18944
2 | GCV ( ADB ) | Kcal/kg | 4188
WTP Report
1 | DM water Generation | m3 | 14 | 230 | 2073
2 | DM water Consumption | m3 | 13 | 230 | 2087
3 | CT Makeup Water Consumption | m3 | 17 | 338 | 2771
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1298
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 399 | 3348
6 | Fly ash to Coal yard(Truck) | nos | 5 | 35 | 344
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 17
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-17 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 180300 | 2969551 | 22695916
2 | Auxiliary power consumption | kWhr | 18170 | 308200 | 2461745
3 | Net Power Exported | kWhr | 162130 | 2661351 | 20234171
4 | Auxiliary power consumption | ( % ) | 10.0776 | 10.3787 | 10.8466
5 | Average Power Generation | MWhr | 7.5125 | 7.2783 | 6.8451
6 | Plant Running Hours | Hrs | 24 | 408 | 3315.66
6 | PLF | ( % ) | 75.125 | 72.7831 | 68.4507
7 | Feed Water consumption | MT | 819 | 13573 | 105346
8 | Boiler Steam Generation | MT | 802 | 13217 | 102205
9 | Bleed steam | MT | 66 | 989 | 6769
10 | Turbine steam consumption | MT | 753 | 12389 | 94562
11 | Condensate Generation | MT | 585 | 9731 | 75344
12 | Auxilairy steam consumption | MT | 17 | 301 | 2450
13 | Specific steam consumption | Kg/Kwhr | 4.1764 | 4.172 | 4.1665
14 | Specific fuel consumption | Kg/Kwhr | 0.72657 | 0.75129 | 0.84046
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.6955 | 2810.2083 | 2806.8132
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3837.9481 | 3840.2771 | 3885.4819
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 131 | 2231 | 19075
2 | GCV ( ADB ) | Kcal/kg | 5270
WTP Report
1 | DM water Generation | m3 | 11 | 241 | 2084
2 | DM water Consumption | m3 | 12 | 242 | 2099
3 | CT Makeup Water Consumption | m3 | 18 | 356 | 2789
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1509
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 28 | 427 | 3376
6 | Fly ash to Coal yard(Truck) | nos | 4 | 39 | 348
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 18
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-18 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 179800 | 3149351 | 22875716
2 | Auxiliary power consumption | kWhr | 18195 | 326395 | 2479940
3 | Net Power Exported | kWhr | 161605 | 2822956 | 20395776
4 | Auxiliary power consumption | ( % ) | 10.1196 | 10.3639 | 10.8409
5 | Average Power Generation | MWhr | 7.4917 | 7.2902 | 6.8497
6 | Plant Running Hours | Hrs | 24 | 432 | 3339.66
6 | PLF | ( % ) | 74.9167 | 72.9016 | 68.4971
7 | Feed Water consumption | MT | 817 | 14390 | 106163
8 | Boiler Steam Generation | MT | 795 | 14012 | 103000
9 | Bleed steam | MT | 66 | 1055 | 6835
10 | Turbine steam consumption | MT | 749 | 13138 | 95311
11 | Condensate Generation | MT | 583 | 10314 | 75927
12 | Auxilairy steam consumption | MT | 18 | 319 | 2468
13 | Specific steam consumption | Kg/Kwhr | 4.1657 | 4.1717 | 4.1665
14 | Specific fuel consumption | Kg/Kwhr | 0.75083 | 0.75127 | 0.83976
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.5451 | 2809.9421 | 2806.8032
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3815.0295 | 3838.8357 | 3884.9281
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 135 | 2366 | 19210
2 | GCV ( ADB ) | Kcal/kg | 4730
WTP Report
1 | DM water Generation | m3 | 13 | 254 | 2097
2 | DM water Consumption | m3 | 12 | 254 | 2111
3 | CT Makeup Water Consumption | m3 | 20 | 376 | 2809
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1423
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 43 | 470 | 3419
6 | Fly ash to Coal yard(Truck) | nos | 0 | 39 | 348
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 19
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-19 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176200 | 3325551 | 23051916
2 | Auxiliary power consumption | kWhr | 18119 | 344514 | 2498059
3 | Net Power Exported | kWhr | 158081 | 2981037 | 20553857
4 | Auxiliary power consumption | ( % ) | 10.2832 | 10.3596 | 10.8367
5 | Average Power Generation | MWhr | 7.3417 | 7.2929 | 6.8532
6 | Plant Running Hours | Hrs | 24 | 456 | 3363.66
6 | PLF | ( % ) | 73.4167 | 72.9288 | 68.5322
7 | Feed Water consumption | MT | 806 | 15196 | 106969
8 | Boiler Steam Generation | MT | 785 | 14797 | 103785
9 | Bleed steam | MT | 65 | 1120 | 6900
10 | Turbine steam consumption | MT | 739 | 13877 | 96050
11 | Condensate Generation | MT | 574 | 10888 | 76501
12 | Auxilairy steam consumption | MT | 18 | 337 | 2486
13 | Specific steam consumption | Kg/Kwhr | 4.1941 | 4.1728 | 4.1667
14 | Specific fuel consumption | Kg/Kwhr | 0.7378 | 0.75055 | 0.83898
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2824.5006 | 2810.7135 | 2806.9385
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3844.0074 | 3839.1097 | 3884.6154
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 130 | 2496 | 19340
2 | GCV ( ADB ) | Kcal/kg | 4275
WTP Report
1 | DM water Generation | m3 | 13 | 267 | 2110
2 | DM water Consumption | m3 | 11 | 265 | 2122
3 | CT Makeup Water Consumption | m3 | 18 | 394 | 2827
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1322
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 45 | 515 | 3464
6 | Fly ash to Coal yard(Truck) | nos | 0 | 39 | 348
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 20
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-20 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 172500 | 3498051 | 23224416
2 | Auxiliary power consumption | kWhr | 18317 | 362831 | 2516376
3 | Net Power Exported | kWhr | 154183 | 3135220 | 20708040
4 | Auxiliary power consumption | ( % ) | 10.6186 | 10.3724 | 10.835
5 | Average Power Generation | MWhr | 7.1875 | 7.2876 | 6.8556
6 | Plant Running Hours | Hrs | 24 | 480 | 3387.66
6 | PLF | ( % ) | 71.875 | 72.8761 | 68.5559
7 | Feed Water consumption | MT | 802 | 15998 | 107771
8 | Boiler Steam Generation | MT | 770 | 15567 | 104555
9 | Bleed steam | MT | 59 | 1179 | 6959
10 | Turbine steam consumption | MT | 724 | 14601 | 96774
11 | Condensate Generation | MT | 572 | 11460 | 77073
12 | Auxilairy steam consumption | MT | 17 | 354 | 2503
13 | Specific steam consumption | Kg/Kwhr | 4.1971 | 4.174 | 4.1669
14 | Specific fuel consumption | Kg/Kwhr | 0.77101 | 0.75156 | 0.83847
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2827.6058 | 2811.5465 | 2807.092
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3851.4307 | 3839.7173 | 3884.3689
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 133 | 2629 | 19473
2 | GCV ( ADB ) | Kcal/kg | 3913
WTP Report
1 | DM water Generation | m3 | 14 | 281 | 2124
2 | DM water Consumption | m3 | 17 | 282 | 2139
3 | CT Makeup Water Consumption | m3 | 9 | 403 | 2836
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1263
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 49 | 564 | 3513
6 | Fly ash to Coal yard(Truck) | nos | 0 | 39 | 348
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 21
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-21 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 169000 | 3667051 | 23393416
2 | Auxiliary power consumption | kWhr | 18275 | 381106 | 2534651
3 | Net Power Exported | kWhr | 150725 | 3285945 | 20858765
4 | Auxiliary power consumption | ( % ) | 10.8136 | 10.3927 | 10.8349
5 | Average Power Generation | MWhr | 7.0417 | 7.2759 | 6.8569
6 | Plant Running Hours | Hrs | 24 | 504 | 3411.66
6 | PLF | ( % ) | 70.4167 | 72.7589 | 68.569
7 | Feed Water consumption | MT | 776 | 16774 | 108547
8 | Boiler Steam Generation | MT | 753 | 16320 | 105308
9 | Bleed steam | MT | 57 | 1236 | 7016
10 | Turbine steam consumption | MT | 708 | 15309 | 97482
11 | Condensate Generation | MT | 554 | 12014 | 77627
12 | Auxilairy steam consumption | MT | 18 | 372 | 2521
13 | Specific steam consumption | Kg/Kwhr | 4.1893 | 4.1747 | 4.1671
14 | Specific fuel consumption | Kg/Kwhr | 0.7574 | 0.75183 | 0.83789
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2822.0947 | 2812.0326 | 2807.2004
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3844.4015 | 3839.9332 | 3884.0801
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 128 | 2757 | 19601
2 | GCV ( ADB ) | Kcal/kg | 4073
1 | DM water Generation | m3 | 15 | 296 | 2139
2 | DM water Consumption | m3 | 15 | 297 | 2154
3 | CT Makeup Water Consumption | m3 | 52 | 455 | 2888
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.5 | 1324
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 25 | 589 | 3538
6 | Fly ash to Coal yard(Truck) | nos | 2 | 41 | 350
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 22
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-22 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 182200 | 3849251 | 23575616
2 | Auxiliary power consumption | kWhr | 18543 | 399649 | 2553194
3 | Net Power Exported | kWhr | 163657 | 3449602 | 21022422
4 | Auxiliary power consumption | ( % ) | 10.1773 | 10.3825 | 10.8298
5 | Average Power Generation | MWhr | 7.5917 | 7.2902 | 6.862
6 | Plant Running Hours | Hrs | 24 | 528 | 3435.66
6 | PLF | ( % ) | 75.9167 | 72.9025 | 68.6203
7 | Feed Water consumption | MT | 824 | 17598 | 109371
8 | Boiler Steam Generation | MT | 805 | 17125 | 106113
9 | Bleed steam | MT | 61 | 1297 | 7077
10 | Turbine steam consumption | MT | 759 | 16068 | 98241
11 | Condensate Generation | MT | 592 | 12606 | 78219
12 | Auxilairy steam consumption | MT | 18 | 390 | 2539
13 | Specific steam consumption | Kg/Kwhr | 4.1658 | 4.1743 | 4.1671
14 | Specific fuel consumption | Kg/Kwhr | 0.75192 | 0.75183 | 0.83722
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.1976 | 2811.7091 | 2807.1849
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3812.1323 | 3838.6172 | 3883.5241
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 137 | 2894 | 19738
2 | GCV ( ADB ) | Kcal/kg | 4015
WTP Report
1 | DM water Generation | m3 | 11 | 307 | 2150
2 | DM water Consumption | m3 | 10 | 307 | 2164
3 | CT Makeup Water Consumption | m3 | 17 | 472 | 2905
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1282
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 32 | 621 | 3570
6 | Fly ash to Coal yard(Truck) | nos | 2 | 43 | 352
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 23
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-23 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 182800 | 4032051 | 23758416
2 | Auxiliary power consumption | kWhr | 18434 | 418083 | 2571628
3 | Net Power Exported | kWhr | 164366 | 3613968 | 21186788
4 | Auxiliary power consumption | ( % ) | 10.0842 | 10.369 | 10.8241
5 | Average Power Generation | MWhr | 7.6167 | 7.3044 | 6.8673
6 | Plant Running Hours | Hrs | 24 | 552 | 3459.66
6 | PLF | ( % ) | 76.1667 | 73.0444 | 68.6727
7 | Feed Water consumption | MT | 833 | 18431 | 110204
8 | Boiler Steam Generation | MT | 806 | 17931 | 106919
9 | Bleed steam | MT | 62 | 1359 | 7139
10 | Turbine steam consumption | MT | 764 | 16832 | 99005
11 | Condensate Generation | MT | 600 | 13206 | 78819
12 | Auxilairy steam consumption | MT | 17 | 407 | 2556
13 | Specific steam consumption | Kg/Kwhr | 4.1794 | 4.1746 | 4.1672
14 | Specific fuel consumption | Kg/Kwhr | 0.74398 | 0.75148 | 0.8365
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2814.3982 | 2811.831 | 2807.2404
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3804.3399 | 3837.0632 | 3882.9149
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 136 | 3030 | 19874
2 | GCV ( ADB ) | Kcal/kg | 4015
WTP Report
1 | DM water Generation | m3 | 11 | 318 | 2161
2 | DM water Consumption | m3 | 10 | 317 | 2174
3 | CT Makeup Water Consumption | m3 | 18 | 490 | 2923
4 | Fly ash combustible/ GCV | % / kcal/kg | 17.9 | 1375
5 | Fly ash to cement mill | MT | 54 | 675 | 3624
6 | Fly ash to Coal yard(Truck) | nos | 0 | 43 | 352
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 24
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-24 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 184900 | 4216951 | 23943316
2 | Auxiliary power consumption | kWhr | 18589 | 436672 | 2590217
3 | Net Power Exported | kWhr | 166311 | 3780279 | 21353099
4 | Auxiliary power consumption | ( % ) | 10.0535 | 10.3552 | 10.8181
5 | Average Power Generation | MWhr | 7.7042 | 7.3211 | 6.873
6 | Plant Running Hours | Hrs | 24 | 576 | 3483.66
6 | PLF | ( % ) | 77.0417 | 73.211 | 68.7303
7 | Feed Water consumption | MT | 842 | 19273 | 111046
8 | Boiler Steam Generation | MT | 817 | 18748 | 107736
9 | Bleed steam | MT | 62 | 1421 | 7201
10 | Turbine steam consumption | MT | 771 | 17603 | 99776
11 | Condensate Generation | MT | 606 | 13812 | 79425
12 | Auxilairy steam consumption | MT | 18 | 425 | 2574
13 | Specific steam consumption | Kg/Kwhr | 4.1698 | 4.1743 | 4.1672
14 | Specific fuel consumption | Kg/Kwhr | 0.75717 | 0.75173 | 0.83589
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2808.3991 | 2748.1284 | 2741.5326
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3812.4627 | 3835.9846 | 3882.3708
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 140 | 3170 | 20014
2 | GCV ( ADB ) | Kcal/kg | 4215
WTP Report
1 | DM water Generation | m3 | 13 | 331 | 2174
2 | DM water Consumption | m3 | 13 | 330 | 2187
3 | CT Makeup Water Consumption | m3 | 18 | 508 | 2941
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1607
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 53 | 728 | 3677
6 | Fly ash to Coal yard(Truck) | nos | 0 | 43 | 352
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 25
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-25 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178500 | 4395451 | 24121816
2 | Auxiliary power consumption | kWhr | 18430 | 455102 | 2608647
3 | Net Power Exported | kWhr | 160070 | 3940349 | 21513169
4 | Auxiliary power consumption | ( % ) | 10.3249 | 10.3539 | 10.8145
5 | Average Power Generation | MWhr | 7.4375 | 7.3258 | 6.8769
6 | Plant Running Hours | Hrs | 24 | 600 | 3507.66
6 | PLF | ( % ) | 74.375 | 73.2575 | 68.769
7 | Feed Water consumption | MT | 827 | 20100 | 111873
8 | Boiler Steam Generation | MT | 789 | 19537 | 108525
9 | Bleed steam | MT | 61 | 1482 | 7262
10 | Turbine steam consumption | MT | 746 | 18349 | 100522
11 | Condensate Generation | MT | 596 | 14408 | 80021
12 | Auxilairy steam consumption | MT | 18 | 443 | 2592
13 | Specific steam consumption | Kg/Kwhr | 4.1793 | 4.1745 | 4.1673
14 | Specific fuel consumption | Kg/Kwhr | 0.7507 | 0.75169 | 0.83526
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.1793 | 2811.8632 | 2807.3154
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3813.8117 | 3835.0841 | 3881.8635
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 134 | 3304 | 20148
2 | GCV ( ADB ) | Kcal/kg | 4174
WTP Report
1 | DM water Generation | m3 | 21 | 352 | 2195
2 | DM water Consumption | m3 | 21 | 351 | 2208
3 | CT Makeup Water Consumption | m3 | 18 | 526 | 2959
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.8 | 1510
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 50 | 778 | 3727
6 | Fly ash to Coalyard(Truck) | nos | 0 | 43 | 352
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 26
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-26 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 158600 | 4554051 | 24280416
2 | Auxiliary power consumption | kWhr | 17975 | 473077 | 2626622
3 | Net Power Exported | kWhr | 140625 | 4080974 | 21653794
4 | Auxiliary power consumption | ( % ) | 11.3335 | 10.388 | 10.8179
5 | Average Power Generation | MWhr | 6.6083 | 7.2982 | 6.8751
6 | Plant Running Hours | Hrs | 24 | 624 | 3531.66
6 | PLF | ( % ) | 66.0833 | 72.9816 | 68.7507
7 | Feed Water consumption | MT | 754 | 20854 | 112627
8 | Boiler Steam Generation | MT | 730 | 20267 | 109255
9 | Bleed steam | MT | 41 | 1523 | 7303
10 | Turbine steam consumption | MT | 666 | 19015 | 101188
11 | Condensate Generation | MT | 539 | 14947 | 80560
12 | Auxilairy steam consumption | MT | 17 | 460 | 2609
13 | Specific steam consumption | Kg/Kwhr | 4.1992 | 4.1754 | 4.1675
14 | Specific fuel consumption | Kg/Kwhr | 0.74401 | 0.75142 | 0.83466
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2828.739 | 2812.4509 | 2807.4554
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3971.3681 | 3839.8304 | 3882.4481
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 118 | 3422 | 20266
2 | GCV ( ADB ) | Kcal/kg | 4192
WTP Report
1 | DM water Generation | m3 | 15 | 367 | 2210
2 | DM water Consumption | m3 | 14 | 365 | 2222
3 | CT Makeup Water Consumption | m3 | 58 | 584 | 3017
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1575
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 43 | 821 | 3770
6 | Fly ash to Coalyard(Truck) | nos | 0 | 43 | 352
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 27
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-27 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 169800 | 4723851 | 24450216
2 | Auxiliary power consumption | kWhr | 18235 | 491312 | 2644857
3 | Net Power Exported | kWhr | 151565 | 4232539 | 21805359
4 | Auxiliary power consumption | ( % ) | 10.7391 | 10.4007 | 10.8173
5 | Average Power Generation | MWhr | 7.075 | 7.2899 | 6.8764
6 | Plant Running Hours | Hrs | 24 | 648 | 3555.66
6 | PLF | ( % ) | 70.75 | 72.8989 | 68.7642
7 | Feed Water consumption | MT | 791 | 21645 | 113418
8 | Boiler Steam Generation | MT | 757 | 21024 | 110012
9 | Bleed steam | MT | 55 | 1578 | 7358
10 | Turbine steam consumption | MT | 710 | 19725 | 101898
11 | Condensate Generation | MT | 566 | 15513 | 81126
12 | Auxilairy steam consumption | MT | 18 | 478 | 2627
13 | Specific steam consumption | Kg/Kwhr | 4.1814 | 4.1756 | 4.1676
14 | Specific fuel consumption | Kg/Kwhr | 0.74794 | 0.75129 | 0.83406
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.9022 | 2812.6109 | 2807.521
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3846.6144 | 3840.0742 | 3882.1993
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 127 | 3549 | 20393
2 | GCV ( ADB ) | Kcal/kg | 4288
WTP Report
1 | DM water Generation | m3 | 14 | 381 | 2224
2 | DM water Consumption | m3 | 16 | 381 | 2238
3 | CT Makeup Water Consumption | m3 | 18 | 602 | 3035
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1542
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 37 | 858 | 3807
6 | Fly ash to Coalyard(Truck) | nos | 1 | 44 | 353
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 28
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-28 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 136500 | 4860351 | 24586716
2 | Auxiliary power consumption | kWhr | 17502 | 508814 | 2662359
3 | Net Power Exported | kWhr | 118998 | 4351537 | 21924357
4 | Auxiliary power consumption | ( % ) | 12.822 | 10.4687 | 10.8284
5 | Average Power Generation | MWhr | 5.6875 | 7.2327 | 6.8685
6 | Plant Running Hours | Hrs | 24 | 672 | 3579.66
6 | PLF | ( % ) | 56.875 | 72.3267 | 68.6845
7 | Feed Water consumption | MT | 677 | 22322 | 114095
8 | Boiler Steam Generation | MT | 658 | 21682 | 110670
9 | Bleed steam | MT | 25 | 1603 | 7383
10 | Turbine steam consumption | MT | 572 | 20297 | 102470
11 | Condensate Generation | MT | 480 | 15993 | 81606
12 | Auxilairy steam consumption | MT | 18 | 496 | 2645
13 | Specific steam consumption | Kg/Kwhr | 4.1905 | 4.176 | 4.1677
14 | Specific fuel consumption | Kg/Kwhr | 0.71795 | 0.75036 | 0.83342
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2823.0476 | 2812.904 | 2807.6072
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4159.2373 | 3849.0377 | 3883.7373
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 98 | 3647 | 20491
2 | GCV ( ADB ) | Kcal/kg | 5490
WTP Report
1 | DM water Generation | m3 | 14 | 395 | 2238
2 | DM water Consumption | m3 | 13 | 394 | 2251
3 | CT Makeup Water Consumption | m3 | 18 | 620 | 3053
4 | Fly ash combustible/ GCV | % / kcal/kg | 26 | 1845
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 858 | 3807
6 | Fly ash to Coalyard(Truck) | nos | 4 | 48 | 357
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 29
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-29 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 104100 | 4964451 | 24690816
2 | Auxiliary power consumption | kWhr | 16914 | 525728 | 2679273
3 | Net Power Exported | kWhr | 87186 | 4438723 | 22011543
4 | Auxiliary power consumption | ( % ) | 16.2478 | 10.5899 | 10.8513
5 | Average Power Generation | MWhr | 4.3375 | 7.1328 | 6.8516
6 | Plant Running Hours | Hrs | 24 | 696 | 3603.66
6 | PLF | ( % ) | 43.375 | 71.3283 | 68.5159
7 | Feed Water consumption | MT | 573 | 22895 | 114668
8 | Boiler Steam Generation | MT | 530 | 22212 | 111200
9 | Bleed steam | MT | 0 | 1603 | 7383
10 | Turbine steam consumption | MT | 444 | 20741 | 102914
11 | Condensate Generation | MT | 429 | 16422 | 82035
12 | Auxilairy steam consumption | MT | 18 | 514 | 2663
13 | Specific steam consumption | Kg/Kwhr | 4.2651 | 4.1779 | 4.1681
14 | Specific fuel consumption | Kg/Kwhr | 0.76849 | 0.75074 | 0.83314
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2873.8905 | 2814.1829 | 2807.8866
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4392.8422 | 3860.4408 | 3885.8838
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 80 | 3727 | 20571
2 | GCV ( ADB ) | Kcal/kg | 5211
WTP Report
1 | DM water Generation | m3 | 12 | 407 | 2250
2 | DM water Consumption | m3 | 12 | 406 | 2263
3 | CT Makeup Water Consumption | m3 | 15 | 635 | 3068
4 | Fly ash combustible/ GCV | % / kcal/kg | 26 | 2027
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 858 | 3807
6 | Fly ash to Coalyard(Truck) | nos | 3 | 51 | 360
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 30
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 155400 | 5119851 | 24846216
2 | Auxiliary power consumption | kWhr | 18007 | 543735 | 2697280
3 | Net Power Exported | kWhr | 137393 | 4576116 | 22148936
4 | Auxiliary power consumption | ( % ) | 11.5875 | 10.6201 | 10.8559
5 | Average Power Generation | MWhr | 6.475 | 7.1109 | 6.8491
6 | Plant Running Hours | Hrs | 24 | 720 | 3627.66
6 | PLF | ( % ) | 64.75 | 71.109 | 68.491
7 | Feed Water consumption | MT | 736 | 23631 | 115404
8 | Boiler Steam Generation | MT | 706 | 22918 | 111906
9 | Bleed steam | MT | 48 | 1651 | 7431
10 | Turbine steam consumption | MT | 652 | 21393 | 103566
11 | Condensate Generation | MT | 524 | 16946 | 82559
12 | Auxilairy steam consumption | MT | 17 | 531 | 2680
13 | Specific steam consumption | Kg/Kwhr | 4.1956 | 4.1784 | 4.1683
14 | Specific fuel consumption | Kg/Kwhr | 0.75933 | 0.751 | 0.83268
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2828.0952 | 2814.6052 | 2808.013
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3919.8924 | 3862.2453 | 3886.0965
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 118 | 3845 | 20689
2 | GCV ( ADB ) | Kcal/kg | 4417
WTP Report
1 | DM water Generation | m3 | 23 | 430 | 2273
2 | DM water Consumption | m3 | 23 | 429 | 2286
3 | CT Makeup Water Consumption | m3 | 18 | 653 | 3086
4 | Fly ash combustible/ GCV | % / kcal/kg | 22 | 1822
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 858 | 3807
6 | Fly ash to Coalyard(Truck) | nos | 5 | 56 | 365
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 31
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-08-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 174200 | 5294051 | 25020416
2 | Auxiliary power consumption | kWhr | 18213 | 561948 | 2715493
3 | Net Power Exported | kWhr | 155987 | 4732103 | 22304923
4 | Auxiliary power consumption | ( % ) | 10.4552 | 10.6147 | 10.8531
5 | Average Power Generation | MWhr | 7.2583 | 7.1157 | 6.8518
6 | Plant Running Hours | Hrs | 24 | 744 | 3651.66
6 | PLF | ( % ) | 72.5833 | 71.1566 | 68.5179
7 | Feed Water consumption | MT | 794 | 24425 | 116198
8 | Boiler Steam Generation | MT | 771 | 23689 | 112677
9 | Bleed steam | MT | 57 | 1708 | 7488
10 | Turbine steam consumption | MT | 726 | 22119 | 104292
11 | Condensate Generation | MT | 570 | 17516 | 83129
12 | Auxilairy steam consumption | MT | 18 | 549 | 2698
13 | Specific steam consumption | Kg/Kwhr | 4.1676 | 4.1781 | 4.1683
14 | Specific fuel consumption | Kg/Kwhr | 0.75775 | 0.75122 | 0.83216
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.5327 | 2814.3395 | 2808.0027
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3818.798 | 3860.8157 | 3885.6279
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 132 | 3977 | 20821
2 | GCV ( ADB ) | Kcal/kg | 4601
WTP Report
1 | DM water Generation | m3 | 11 | 441 | 2284
2 | DM water Consumption | m3 | 10 | 439 | 2296
3 | CT Makeup Water Consumption | m3 | 18 | 671 | 3104
4 | Fly ash combustible/ GCV | % / kcal/kg | 19.9 | 1650
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 858 | 3807
6 | Fly ash to Coalyard(Truck) | nos | 4 | 60 | 369
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0