## 0
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-06-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 130600 | 5030865 | 14319965
2 | Auxiliary power consumption | kWhr | 17516 | 544111 | 1602595
3 | Net Power Exported | kWhr | 113084 | 4486754 | 12717370
4 | Auxiliary power consumption | ( % ) | 13.4119 | 10.8155 | 11.1913
5 | Average Power Generation | MWhr | 5.8044 | 7.0165 | 6.6184
6 | Plant Running Hours | Hrs | 22.5 | 717 | 2163.66
6 | PLF | ( % ) | 58.0444 | 70.1655 | 66.184
7 | Feed Water consumption | MT | 675 | 23312 | 67000
8 | Boiler Steam Generation | MT | 637 | 22524 | 64913
9 | Bleed steam | MT | 21 | 1643 | 4088
10 | Turbine steam consumption | MT | 543 | 21012 | 59626
11 | Condensate Generation | MT | 462 | 16678 | 47884
12 | Auxilairy steam consumption | MT | 18 | 534 | 1615
13 | Specific steam consumption | Kg/Kwhr | 4.1577 | 4.1766 | 4.1638
14 | Specific fuel consumption | Kg/Kwhr | 0.93415 | 0.85234 | 0.87011
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2807.343 | 2813.732 | 2805.2958
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4208.3971 | 3862.9876 | 3911.2015
17 | DG Power Generation | kWhr | 1468 | 1468 | 1468
FUEL Report
1 | Coal Consumption | MT | 122 | 4288 | 12460
2 | GCV ( ADB ) | Kcal/kg | 4509
WTP Report
1 | DM water Generation | m3 | 41 | 478 | 1433
2 | DM water Consumption | m3 | 40 | 481 | 1448
3 | CT Makeup Water Consumption | m3 | 18 | 646 | 1782
4 | Fly ash combustible/ GCV | % / kcal/kg | 20.62 | 1421
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 787 | 2158
6 | Fly ash to Coalyard(Truck) | nos | 2 | 61 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 1
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-01 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 129200 | 129200 | 14449165
2 | Auxiliary power consumption | kWhr | 17267 | 17267 | 1619862
3 | Net Power Exported | kWhr | 111933 | 111933 | 12829303
4 | Auxiliary power consumption | ( % ) | 13.3646 | 13.3646 | 11.2108
5 | Average Power Generation | MWhr | 5.3833 | 5.3833 | 6.6048
6 | Plant Running Hours | Hrs | 24 | 24 | 2187.66
6 | PLF | ( % ) | 53.8333 | 53.8333 | 66.0485
7 | Feed Water consumption | MT | 642 | 642 | 67642
8 | Boiler Steam Generation | MT | 597 | 597 | 65510
9 | Bleed steam | MT | 25 | 25 | 4113
10 | Turbine steam consumption | MT | 539 | 539 | 60165
11 | Condensate Generation | MT | 446 | 446 | 48330
12 | Auxilairy steam consumption | MT | 17 | 17 | 1632
13 | Specific steam consumption | Kg/Kwhr | 4.1718 | 4.1718 | 4.1639
14 | Specific fuel consumption | Kg/Kwhr | 0.80495 | 0.80495 | 0.86953
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2812.0511 | 2812.0511 | 2805.3562
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3986.8719 | 3986.8719 | 3911.8781
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 104 | 104 | 12564
2 | GCV ( ADB ) | Kcal/kg | 4976
WTP Report
1 | DM water Generation | m2 | 18 | 18 | 1451
2 | DM water Consumption | m3 | 19 | 19 | 1467
3 | CT Makeup Water Consumption | m3 | 18 | 18 | 1800
4 | Fly ash combustible/ GCV | % / kcal/kg | 22.88 | 1745
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 30 | 30 | 2188
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 2
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-02 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 106300 | 235500 | 14555465
2 | Auxiliary power consumption | kWhr | 16786 | 34053 | 1636648
3 | Net Power Exported | kWhr | 89514 | 201447 | 12918817
4 | Auxiliary power consumption | ( % ) | 15.7912 | 14.4599 | 11.2442
5 | Average Power Generation | MWhr | 4.4292 | 4.9062 | 6.5812
6 | Plant Running Hours | Hrs | 24 | 48 | 2211.66
7 | PLF | ( % ) | 44.2917 | 49.0625 | 65.8124
8 | Feed Water consumption | MT | 573 | 1215 | 68215
9 | Boiler Steam Generation | MT | 522 | 1119 | 66032
10 | Bleed steam | MT | 9 | 34 | 4122
11 | Turbine steam consumption | MT | 450 | 989 | 60615
12 | Condensate Generation | MT | 393 | 839 | 48723
13 | Auxilairy steam consumption | MT | 19 | 36 | 1651
14 | Specific steam consumption | Kg/Kwhr | 4.2333 | 4.1996 | 4.1644
15 | Specific fuel consumption | Kg/Kwhr | 0.79962 | 0.80255 | 0.86902
16 | Heat Rate(TG)2880 | Kcal/Kwh | 2853.2455 | 2830.6454 | 2805.706
17 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 4236.9925 | 4099.7714 | 3914.2524
18 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 85 | 189 | 12649
2 | GCV ( ADB ) | Kcal/kg | 5294
WTP Report
1 | DM water Generation | m3 | 14 | 32 | 1465
2 | DM water Consumption | m3 | 15 | 34 | 1482
3 | CT Makeup Water Consumption | m3 | 18 | 36 | 1818
4 | Fly ash combustible/ GCV | % / kcal/kg | 33.67 | 2157
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 20 | 50 | 2208
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 3
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-03 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 183400 | 418900 | 14738865
2 | Auxiliary power consumption | kWhr | 17971 | 52024 | 1654619
3 | Net Power Exported | kWhr | 165429 | 366876 | 13084246
4 | Auxiliary power consumption | ( % ) | 9.7988 | 12.4192 | 11.2262
5 | Average Power Generation | MWhr | 7.6417 | 5.8181 | 6.5926
6 | Plant Running Hours | Hrs | 24 | 72 | 2235.66
6 | PLF | ( % ) | 76.4167 | 58.1806 | 65.9262
7 | Feed Water consumption | MT | 836 | 2051 | 69051
8 | Boiler Steam Generation | MT | 820 | 1939 | 66852
9 | Bleed steam | MT | 53 | 87 | 4175
10 | Turbine steam consumption | MT | 758 | 1747 | 61373
11 | Condensate Generation | MT | 595 | 1434 | 49318
12 | Auxilairy steam consumption | MT | 18 | 54 | 1669
13 | Specific steam consumption | Kg/Kwhr | 4.133 | 4.1704 | 4.164
14 | Specific fuel consumption | Kg/Kwhr | 0.83969 | 0.81881 | 0.86866
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2783.5005 | 2810.0048 | 2805.4297
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3857.758 | 3993.8147 | 3913.5494
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 154 | 343 | 12803
2 | GCV ( ADB ) | Kcal/kg | 4570
WTP Report
1 | DM water Generation | m3 | 11 | 43 | 1476
2 | DM water Consumption | m3 | 12 | 46 | 1494
3 | CT Makeup Water Consumption | m3 | 18 | 54 | 1836
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1396
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 54 | 104 | 2262
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 4
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-04 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 176500 | 595400 | 14915365
2 | Auxiliary power consumption | kWhr | 17747 | 69771 | 1672366
3 | Net Power Exported | kWhr | 158753 | 525629 | 13242999
4 | Auxiliary power consumption | ( % ) | 10.055 | 11.7183 | 11.2124
5 | Average Power Generation | MWhr | 7.3542 | 6.2021 | 6.6007
6 | Plant Running Hours | Hrs | 24 | 96 | 2259.66
6 | PLF | ( % ) | 73.5417 | 62.0208 | 66.0071
7 | Feed Water consumption | MT | 809 | 2860 | 69860
8 | Boiler Steam Generation | MT | 785 | 2724 | 67637
9 | Bleed steam | MT | 59 | 146 | 4234
10 | Turbine steam consumption | MT | 735 | 2482 | 62108
11 | Condensate Generation | MT | 576 | 2010 | 49894
12 | Auxilairy steam consumption | MT | 17 | 71 | 1686
13 | Specific steam consumption | Kg/Kwhr | 4.1643 | 4.1686 | 4.164
14 | Specific fuel consumption | Kg/Kwhr | 0.83853 | 0.82466 | 0.8683
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.1275 | 2808.559 | 2805.4261
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3837.4737 | 3947.4691 | 3912.6492
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 148 | 491 | 12951
2 | GCV ( ADB ) | Kcal/kg | 4565
WTP Report
1 | DM water Generation | m3 | 18 | 61 | 1494
2 | DM water Consumption | m3 | 15 | 61 | 1509
3 | CT Makeup Water Consumption | m3 | 18 | 72 | 1854
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1363
5 | Fly ash to cement mill | MT | 51 | 155 | 2313
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 5
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-05 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 190000 | 785400 | 15105365
2 | Auxiliary power consumption | kWhr | 17950 | 87721 | 1690316
3 | Net Power Exported | kWhr | 172050 | 697679 | 13415049
4 | Auxiliary power consumption | ( % ) | 9.4474 | 11.169 | 11.1902
5 | Average Power Generation | MWhr | 7.9167 | 6.545 | 6.6145
6 | Plant Running Hours | Hrs | 24 | 120 | 2283.66
6 | PLF | ( % ) | 79.1667 | 65.45 | 66.1454
7 | Feed Water consumption | MT | 857 | 3717 | 70717
8 | Boiler Steam Generation | MT | 840 | 3564 | 68477
9 | Bleed steam | MT | 67 | 213 | 4301
10 | Turbine steam consumption | MT | 793 | 3275 | 62901
11 | Condensate Generation | MT | 612 | 2622 | 50506
12 | Auxilairy steam consumption | MT | 18 | 89 | 1704
13 | Specific steam consumption | Kg/Kwhr | 4.1737 | 4.1698 | 4.1641
14 | Specific fuel consumption | Kg/Kwhr | 0.84211 | 0.82888 | 0.86797
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2810.6263 | 2809.0591 | 2805.4915
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3814.5749 | 3915.32 | 3911.4156
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 160 | 651 | 13111
2 | GCV ( ADB ) | Kcal/kg | 4525
WTP Report
1 | DM water Generation | m3 | 10 | 71 | 1504
2 | DM water Consumption | m3 | 11 | 72 | 1520
3 | CT Makeup Water Consumption | m3 | 18 | 90 | 1872
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1261
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 60 | 215 | 2373
6 | Fly ash to Coal yard(Truck) | nos | 0 | 0 | 216
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 6
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-06 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 170000 | 955400 | 15275365
2 | Auxiliary power consumption | kWhr | 17602 | 105323 | 1707918
3 | Net Power Exported | kWhr | 152398 | 850077 | 13567447
4 | Auxiliary power consumption | ( % ) | 10.3541 | 11.024 | 11.1809
5 | Average Power Generation | MWhr | 7.0833 | 6.6347 | 6.6194
6 | Plant Running Hours | Hrs | 24 | 144 | 2307.66
6 | PLF | ( % ) | 70.8333 | 66.3472 | 66.1942
7 | Feed Water consumption | MT | 780 | 4497 | 71497
8 | Boiler Steam Generation | MT | 756 | 4320 | 69233
9 | Bleed steam | MT | 57 | 270 | 4358
10 | Turbine steam consumption | MT | 715 | 3990 | 63616
11 | Condensate Generation | MT | 554 | 3176 | 51060
12 | Auxilairy steam consumption | MT | 18 | 107 | 1722
13 | Specific steam consumption | Kg/Kwhr | 4.2059 | 4.1763 | 4.1646
14 | Specific fuel consumption | Kg/Kwhr | 0.86471 | 0.83525 | 0.86793
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2833.0294 | 2813.3243 | 2805.798
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3837.0136 | 3901.3865 | 3910.5876
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 147 | 798 | 13258
2 | GCV ( ADB ) | Kcal/kg | 4414
WTP Report
1 | DM water Generation | m3 | 15 | 86 | 1519
2 | DM water Consumption | m3 | 14 | 86 | 1534
3 | CT Makeup Water Consumption | m3 | 18 | 108 | 1890
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1258
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 18 | 233 | 2391
6 | Fly ash to Coal yard(Truck) | nos | 4 | 4 | 220
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 7
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-07 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 164100 | 1119500 | 15439465
2 | Auxiliary power consumption | kWhr | 17598 | 122921 | 1725516
3 | Net Power Exported | kWhr | 146502 | 996579 | 13713949
4 | Auxiliary power consumption | ( % ) | 10.7239 | 10.98 | 11.176
5 | Average Power Generation | MWhr | 6.8375 | 6.6637 | 6.6217
6 | Plant Running Hours | Hrs | 24 | 168 | 2331.66
6 | PLF | ( % ) | 68.375 | 66.6369 | 66.2166
7 | Feed Water consumption | MT | 756 | 5253 | 72253
8 | Boiler Steam Generation | MT | 734 | 5054 | 69967
9 | Bleed steam | MT | 54 | 324 | 4412
10 | Turbine steam consumption | MT | 689 | 4679 | 64305
11 | Condensate Generation | MT | 536 | 3712 | 51596
12 | Auxilairy steam consumption | MT | 17 | 124 | 1739
13 | Specific steam consumption | Kg/Kwhr | 4.1987 | 4.1795 | 4.165
14 | Specific fuel consumption | Kg/Kwhr | 0.84095 | 0.83609 | 0.86765
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2828.0743 | 2815.4864 | 2806.0347
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3859.2947 | 3895.2165 | 3910.0424
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 138 | 936 | 13396
2 | GCV ( ADB ) | Kcal/kg | 4587
1 | DM water Generation | m3 | 12 | 98 | 1531
2 | DM water Consumption | m3 | 13 | 99 | 1547
3 | CT Makeup Water Consumption | m3 | 23 | 131 | 1913
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1396
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 280 | 2438
6 | Fly ash to Coal yard(Truck) | nos | 0 | 4 | 220
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 8
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-08 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 158800 | 1278300 | 15598265
2 | Auxiliary power consumption | kWhr | 17416 | 140337 | 1742932
3 | Net Power Exported | kWhr | 141384 | 1137963 | 13855333
4 | Auxiliary power consumption | ( % ) | 10.9673 | 10.9784 | 11.1739
5 | Average Power Generation | MWhr | 6.6167 | 6.6578 | 6.6216
6 | Plant Running Hours | Hrs | 24 | 192 | 2355.66
6 | PLF | ( % ) | 66.1667 | 66.5781 | 66.2161
7 | Feed Water consumption | MT | 738 | 5991 | 72991
8 | Boiler Steam Generation | MT | 714 | 5768 | 70681
9 | Bleed steam | MT | 42 | 366 | 4454
10 | Turbine steam consumption | MT | 658 | 5337 | 64963
11 | Condensate Generation | MT | 533 | 4245 | 52129
12 | Auxilairy steam consumption | MT | 18 | 142 | 1757
13 | Specific steam consumption | Kg/Kwhr | 4.1436 | 4.1751 | 4.1648
14 | Specific fuel consumption | Kg/Kwhr | 0.83753 | 0.83627 | 0.86734
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2791.6499 | 2812.5252 | 2805.8883
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3879.4323 | 3893.2557 | 3909.7308
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 133 | 1069 | 13529
2 | GCV ( ADB ) | Kcal/kg | 4626
WTP Report
1 | DM water Generation | m3 | 17 | 115 | 1548
2 | DM water Consumption | m3 | 16 | 115 | 1563
3 | CT Makeup Water Consumption | m3 | 54 | 185 | 1967
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1387
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 45 | 325 | 2483
6 | Fly ash to Coal yard(Truck) | nos | 0 | 4 | 220
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 9
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-09 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165600 | 1443900 | 15763865
2 | Auxiliary power consumption | kWhr | 17402 | 157739 | 1760334
3 | Net Power Exported | kWhr | 148198 | 1286161 | 14003531
4 | Auxiliary power consumption | ( % ) | 10.5085 | 10.9245 | 11.1669
5 | Average Power Generation | MWhr | 6.9 | 6.6847 | 6.6244
6 | Plant Running Hours | Hrs | 24 | 216 | 2379.66
6 | PLF | ( % ) | 69 | 66.8472 | 66.2442
7 | Feed Water consumption | MT | 760 | 6751 | 73751
8 | Boiler Steam Generation | MT | 740 | 6508 | 71421
9 | Bleed steam | MT | 50 | 416 | 4504
10 | Turbine steam consumption | MT | 690 | 6027 | 65653
11 | Condensate Generation | MT | 547 | 4792 | 52676
12 | Auxilairy steam consumption | MT | 18 | 160 | 1775
13 | Specific steam consumption | Kg/Kwhr | 4.1667 | 4.1741 | 4.1648
14 | Specific fuel consumption | Kg/Kwhr | 0.83937 | 0.83662 | 0.86705
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.7029 | 2811.8575 | 2805.8968
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3855.5989 | 3888.9368 | 3909.1621
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 139 | 1208 | 13668
2 | GCV ( ADB ) | Kcal/kg | 4592
WTP Report
1 | DM water Generation | m3 | 15 | 130 | 1563
2 | DM water Consumption | m3 | 14 | 129 | 1577
3 | CT Makeup Water Consumption | m3 | 20 | 205 | 1987
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.5 | 1344
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 26 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 2 | 6 | 222
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 10
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-10 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165400 | 1609300 | 15929265
2 | Auxiliary power consumption | kWhr | 17476 | 175215 | 1777810
3 | Net Power Exported | kWhr | 147924 | 1434085 | 14151455
4 | Auxiliary power consumption | ( % ) | 10.5659 | 10.8877 | 11.1607
5 | Average Power Generation | MWhr | 6.8917 | 6.7054 | 6.6271
6 | Plant Running Hours | Hrs | 24 | 240 | 2403.66
6 | PLF | ( % ) | 68.9167 | 67.0542 | 66.2709
7 | Feed Water consumption | MT | 755 | 7506 | 74506
8 | Boiler Steam Generation | MT | 741 | 7249 | 72162
9 | Bleed steam | MT | 52 | 468 | 4556
10 | Turbine steam consumption | MT | 690 | 6717 | 66343
11 | Condensate Generation | MT | 541 | 5333 | 53217
12 | Auxilairy steam consumption | MT | 18 | 178 | 1793
13 | Specific steam consumption | Kg/Kwhr | 4.1717 | 4.1739 | 4.1649
14 | Specific fuel consumption | Kg/Kwhr | 0.86457 | 0.8395 | 0.86702
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2809.9154 | 2811.6579 | 2805.9386
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3865.4776 | 3886.5258 | 3908.7085
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 143 | 1351 | 13811
2 | GCV ( ADB ) | Kcal/kg | 4470 | 0
WTP Report
1 | DM water Generation | m3 | 12 | 142 | 1575
2 | DM water Consumption | m3 | 13 | 142 | 1590
3 | CT Makeup Water Consumption | m3 | 21 | 226 | 2008
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1320
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 5 | 11 | 227
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 11
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-11 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 175400 | 1784700 | 16104665
2 | Auxiliary power consumption | kWhr | 17691 | 192906 | 1795501
3 | Net Power Exported | kWhr | 157709 | 1591794 | 14309164
4 | Auxiliary power consumption | ( % ) | 10.0861 | 10.8089 | 11.1489
5 | Average Power Generation | MWhr | 7.3083 | 6.7602 | 6.6338
6 | Plant Running Hours | Hrs | 24 | 264 | 2427.66
6 | PLF | ( % ) | 73.0833 | 67.6023 | 66.3382
7 | Feed Water consumption | MT | 792 | 8298 | 75298
8 | Boiler Steam Generation | MT | 776 | 8025 | 72938
9 | Bleed steam | MT | 56 | 524 | 4612
10 | Turbine steam consumption | MT | 727 | 7444 | 67070
11 | Condensate Generation | MT | 568 | 5901 | 53785
12 | Auxilairy steam consumption | MT | 17 | 195 | 1810
13 | Specific steam consumption | Kg/Kwhr | 4.1448 | 4.171 | 4.1646
14 | Specific fuel consumption | Kg/Kwhr | 0.86659 | 0.84216 | 0.86702
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2791.8529 | 2809.7114 | 2805.7852
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.2675 | 3879.7191 | 3907.7126
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 152 | 1503 | 13963
2 | GCV ( ADB ) | Kcal/kg | 4398
WTP Report
1 | DM water Generation | m3 | 16 | 158 | 1591
2 | DM water Consumption | m3 | 14 | 156 | 1604
3 | CT Makeup Water Consumption | m3 | 17 | 243 | 2025
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1298
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 4 | 15 | 231
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 12
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-12 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 172800 | 1957500 | 16277465
2 | Auxiliary power consumption | kWhr | 17568 | 210474 | 1813069
3 | Net Power Exported | kWhr | 155232 | 1747026 | 14464396
4 | Auxiliary power consumption | ( % ) | 10.1667 | 10.7522 | 11.1385
5 | Average Power Generation | MWhr | 7.2 | 6.7969 | 6.6394
6 | Plant Running Hours | Hrs | 24 | 288 | 2451.66
6 | PLF | ( % ) | 72 | 67.9688 | 66.3936
7 | Feed Water consumption | MT | 782 | 9080 | 76080
8 | Boiler Steam Generation | MT | 770 | 8795 | 73708
9 | Bleed steam | MT | 56 | 580 | 4668
10 | Turbine steam consumption | MT | 720 | 8164 | 67790
11 | Condensate Generation | MT | 561 | 6462 | 54346
12 | Auxilairy steam consumption | MT | 18 | 213 | 1828
13 | Specific steam consumption | Kg/Kwhr | 4.1667 | 4.1706 | 4.1647
14 | Specific fuel consumption | Kg/Kwhr | 0.85648 | 0.84342 | 0.8669
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.0764 | 2809.3905 | 2805.7882
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3844.7442 | 3876.6316 | 3907.0441
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 148 | 1651 | 14111
2 | GCV ( ADB ) | Kcal/kg | 4488
WTP Report
1 | DM water Generation | m3 | 12 | 170 | 1603
2 | DM water Consumption | m3 | 11 | 167 | 1615
3 | CT Makeup Water Consumption | m3 | 17 | 260 | 2042
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1321
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 4 | 19 | 235
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 13
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-13 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 164500 | 2122000 | 16441965
2 | Auxiliary power consumption | kWhr | 17591 | 228065 | 1830660
3 | Net Power Exported | kWhr | 146909 | 1893935 | 14611305
4 | Auxiliary power consumption | ( % ) | 10.6936 | 10.7476 | 11.1341
5 | Average Power Generation | MWhr | 6.8542 | 6.8013 | 6.6414
6 | Plant Running Hours | Hrs | 24 | 312 | 2475.66
6 | PLF | ( % ) | 68.5417 | 68.0128 | 66.4145
7 | Feed Water consumption | MT | 762 | 9842 | 76842
8 | Boiler Steam Generation | MT | 735 | 9530 | 74443
9 | Bleed steam | MT | 52 | 632 | 4720
10 | Turbine steam consumption | MT | 699 | 8863 | 68489
11 | Condensate Generation | MT | 547 | 7009 | 54893
12 | Auxilairy steam consumption | MT | 18 | 231 | 1846
13 | Specific steam consumption | Kg/Kwhr | 4.2492 | 4.1767 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.86322 | 0.84496 | 0.86687
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2862.2918 | 2813.4915 | 2806.3536
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3855.1555 | 3874.9668 | 3906.525
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 142 | 1793 | 14253
2 | GCV ( ADB ) | Kcal/kg | 4439
WTP Report
1 | DM water Generation | m3 | 14 | 184 | 1617
2 | DM water Consumption | m3 | 14 | 181 | 1629
3 | CT Makeup Water Consumption | m3 | 18 | 278 | 2060
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1317
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT |  | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 4 | 23 | 239
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 14
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-14 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178100 | 2300100 | 16620065
2 | Auxiliary power consumption | kWhr | 17829 | 245894 | 1848489
3 | Net Power Exported | kWhr | 160271 | 2054206 | 14771576
4 | Auxiliary power consumption | ( % ) | 10.0107 | 10.6906 | 11.122
5 | Average Power Generation | MWhr | 7.4208 | 6.8455 | 6.6489
6 | Plant Running Hours | Hrs | 24 | 336 | 2499.66
6 | PLF | ( % ) | 74.2083 | 68.4554 | 66.4893
7 | Feed Water consumption | MT | 811 | 10653 | 77653
8 | Boiler Steam Generation | MT | 792 | 10322 | 75235
9 | Bleed steam | MT | 59 | 691 | 4779
10 | Turbine steam consumption | MT | 741 | 9604 | 69230
11 | Condensate Generation | MT | 583 | 7592 | 55476
12 | Auxilairy steam consumption | MT | 18 | 249 | 1864
13 | Specific steam consumption | Kg/Kwhr | 4.1606 | 4.1755 | 4.1654
14 | Specific fuel consumption | Kg/Kwhr | 0.85345 | 0.84562 | 0.86672
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2802.4312 | 2812.6351 | 2806.3115
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3836.911 | 3872.0201 | 3905.779
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 152 | 1945 | 14405
2 | GCV ( ADB ) | Kcal/kg | 4494
WTP Report
1 | DM water Generation | m3 | 13 | 197 | 1630
2 | DM water Consumption | m3 | 14 | 195 | 1643
3 | CT Makeup Water Consumption | m3 | 17 | 295 | 2077
4 | Fly ash combustible/ GCV | % / kcal/kg | 17.75 | 1330
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 4 | 27 | 243
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 15
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-15 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 184200 | 2484300 | 16804265
2 | Auxiliary power consumption | kWhr | 18146 | 264040 | 1866635
3 | Net Power Exported | kWhr | 166054 | 2220260 | 14937630
4 | Auxiliary power consumption | ( % ) | 9.8512 | 10.6283 | 11.1081
5 | Average Power Generation | MWhr | 7.675 | 6.9008 | 6.6587
6 | Plant Running Hours | Hrs | 24 | 360 | 2523.66
6 | PLF | ( % ) | 76.75 | 69.0083 | 66.5869
7 | Feed Water consumption | MT | 832 | 11485 | 78485
8 | Boiler Steam Generation | MT | 816 | 11138 | 76051
9 | Bleed steam | MT | 60 | 751 | 4839
10 | Turbine steam consumption | MT | 766 | 10370 | 69996
11 | Condensate Generation | MT | 600 | 8192 | 56076
12 | Auxilairy steam consumption | MT | 18 | 267 | 1882
13 | Specific steam consumption | Kg/Kwhr | 4.1585 | 4.1742 | 4.1654
14 | Specific fuel consumption | Kg/Kwhr | 0.84148 | 0.84531 | 0.86645
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2800.6406 | 2811.7458 | 2806.2494
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3822.2668 | 3868.3311 | 3904.8636
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 155 | 2100 | 14560
2 | GCV ( ADB ) | Kcal/kg | 4542
WTP Report
1 | DM water Generation | m3 | 12 | 209 | 1642
2 | DM water Consumption | m3 | 12 | 207 | 1655
3 | CT Makeup Water Consumption | m3 | 18 | 313 | 2095
4 | Fly ash combustible/ GCV | % / kcal/kg | 16.8 | 1280
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 5 | 32 | 248
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 16
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-16 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 181700 | 2666000 | 16985965
2 | Auxiliary power consumption | kWhr | 17979 | 282019 | 1884614
3 | Net Power Exported | kWhr | 163721 | 2383981 | 15101351
4 | Auxiliary power consumption | ( % ) | 9.8949 | 10.5784 | 11.0951
5 | Average Power Generation | MWhr | 7.5708 | 6.9427 | 6.6673
6 | Plant Running Hours | Hrs | 24 | 384 | 2547.66
6 | PLF | ( % ) | 75.7083 | 69.4271 | 66.6728
7 | Feed Water consumption | MT | 822 | 12307 | 79307
8 | Boiler Steam Generation | MT | 804 | 11942 | 76855
9 | Bleed steam | MT | 60 | 811 | 4899
10 | Turbine steam consumption | MT | 760 | 11130 | 70756
11 | Condensate Generation | MT | 591 | 8783 | 56667
12 | Auxilairy steam consumption | MT | 18 | 285 | 1900
13 | Specific steam consumption | Kg/Kwhr | 4.1827 | 4.1748 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.87507 | 0.84734 | 0.86654
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2816.951 | 2812.1005 | 2806.3638
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.8739 | 3864.8922 | 3903.9331
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 159 | 2259 | 14719
2 | GCV ( ADB ) | Kcal/kg | 4355
WTP Report
1 | DM water Generation | m3 | 12 | 221 | 1654
2 | DM water Consumption | m3 | 12 | 219 | 1667
3 | CT Makeup Water Consumption | m3 | 18 | 331 | 2113
4 | Fly ash combustible/ GCV | % / kcal/kg | 16.57 | 1164
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 6 | 38 | 254
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 17
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-17 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 190400 | 2856400 | 17176365
2 | Auxiliary power consumption | kWhr | 18138 | 300157 | 1902752
3 | Net Power Exported | kWhr | 172262 | 2556243 | 15273613
4 | Auxiliary power consumption | ( % ) | 9.5263 | 10.5082 | 11.0777
5 | Average Power Generation | MWhr | 7.9333 | 7.001 | 6.6791
6 | Plant Running Hours | Hrs | 24 | 408 | 2571.66
6 | PLF | ( % ) | 79.3333 | 70.0098 | 66.791
7 | Feed Water consumption | MT | 856 | 13163 | 80163
8 | Boiler Steam Generation | MT | 839 | 12781 | 77694
9 | Bleed steam | MT | 63 | 874 | 4962
10 | Turbine steam consumption | MT | 792 | 11922 | 71548
11 | Condensate Generation | MT | 616 | 9399 | 57283
12 | Auxilairy steam consumption | MT | 18 | 303 | 1918
13 | Specific steam consumption | Kg/Kwhr | 4.1597 | 4.1738 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.8666 | 0.84862 | 0.86654
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2801.6597 | 2811.4046 | 2806.3117
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3802.0295 | 3860.7019 | 3902.8035
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 165 | 2424 | 14884
2 | GCV ( ADB ) | Kcal/kg | 4387
WTP Report
1 | DM water Generation | m3 | 13 | 234 | 1667
2 | DM water Consumption | m3 | 14 | 233 | 1681
3 | CT Makeup Water Consumption | m3 | 20 | 351 | 2133
4 | Fly ash combustible/ GCV | % / kcal/kg | 15 | 1145
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 6 | 44 | 260
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 18
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-18 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 184200 | 3040600 | 17360565
2 | Auxiliary power consumption | kWhr | 18147 | 318304 | 1920899
3 | Net Power Exported | kWhr | 166053 | 2722296 | 15439666
4 | Auxiliary power consumption | ( % ) | 9.8518 | 10.4685 | 11.0647
5 | Average Power Generation | MWhr | 7.675 | 7.0384 | 6.6883
6 | Plant Running Hours | Hrs | 24 | 432 | 2595.66
6 | PLF | ( % ) | 76.75 | 70.3843 | 66.883
7 | Feed Water consumption | MT | 828 | 13991 | 80991
8 | Boiler Steam Generation | MT | 815 | 13596 | 78509
9 | Bleed steam | MT | 60 | 934 | 5022
10 | Turbine steam consumption | MT | 760 | 12682 | 72308
11 | Condensate Generation | MT | 593 | 9992 | 57876
12 | Auxilairy steam consumption | MT | 17 | 320 | 1935
13 | Specific steam consumption | Kg/Kwhr | 4.126 | 4.1709 | 4.1651
14 | Specific fuel consumption | Kg/Kwhr | 0.81976 | 0.84687 | 0.86604
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2778.3931 | 2809.4047 | 2806.0155
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.5826 | 3858.0897 | 3901.8993
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 151 | 2575 | 15035
2 | GCV ( ADB ) | Kcal/kg | 4642
WTP Report
1 | DM water Generation | m3 | 11 | 245 | 1678
2 | DM water Consumption | m3 | 10 | 243 | 1691
3 | CT Makeup Water Consumption | m3 | 17 | 368 | 2150
4 | Fly ash combustible/ GCV | % / kcal/kg | 15.8 | 1286
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 4 | 48 | 264
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 19
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-19 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 186600 | 3227200 | 17547165
2 | Auxiliary power consumption | kWhr | 17626 | 335930 | 1938525
3 | Net Power Exported | kWhr | 168974 | 2891270 | 15608640
4 | Auxiliary power consumption | ( % ) | 9.4459 | 10.4093 | 11.0475
5 | Average Power Generation | MWhr | 7.775 | 7.0772 | 6.6983
6 | Plant Running Hours | Hrs | 24 | 456 | 2619.66
6 | PLF | ( % ) | 77.75 | 70.7719 | 66.9826
7 | Feed Water consumption | MT | 851 | 14842 | 81842
8 | Boiler Steam Generation | MT | 825 | 14421 | 79334
9 | Bleed steam | MT | 63 | 997 | 5085
10 | Turbine steam consumption | MT | 785 | 13467 | 73093
11 | Condensate Generation | MT | 611 | 10603 | 58487
12 | Auxilairy steam consumption | MT | 18 | 338 | 1953
13 | Specific steam consumption | Kg/Kwhr | 4.2069 | 4.173 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.81994 | 0.84531 | 0.86555
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2832.985 | 2810.7682 | 2806.3023
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3814.7209 | 3855.5821 | 3900.9722
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 153 | 2728 | 15188
2 | GCV ( ADB ) | Kcal/kg | 4630
WTP Report
1 | DM water Generation | m3 | 10 | 255 | 1688
2 | DM water Consumption | m3 | 11 | 254 | 1702
3 | CT Makeup Water Consumption | m3 | 18 | 386 | 2168
4 | Fly ash combustible/ GCV | % / kcal/kg | 15.5 | 1280
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 5 | 53 | 269
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 20
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-20 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 165500 | 3392700 | 17712665
2 | Auxiliary power consumption | kWhr | 17743 | 353673 | 1956268
3 | Net Power Exported | kWhr | 147757 | 3039027 | 15756397
4 | Auxiliary power consumption | ( % ) | 10.7208 | 10.4245 | 11.0445
5 | Average Power Generation | MWhr | 6.8958 | 7.0681 | 6.7001
6 | Plant Running Hours | Hrs | 24 | 480 | 2643.66
6 | PLF | ( % ) | 68.9583 | 70.6813 | 67.0005
7 | Feed Water consumption | MT | 763 | 15605 | 82605
8 | Boiler Steam Generation | MT | 740 | 15161 | 80074
9 | Bleed steam | MT | 49 | 1046 | 5134
10 | Turbine steam consumption | MT | 683 | 14150 | 73776
11 | Condensate Generation | MT | 542 | 11145 | 59029
12 | Auxilairy steam consumption | MT | 18 | 356 | 1971
13 | Specific steam consumption | Kg/Kwhr | 4.1269 | 4.1707 | 4.1652
14 | Specific fuel consumption | Kg/Kwhr | 0.83988 | 0.84505 | 0.86531
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2780.1148 | 2809.2729 | 2806.0576
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3857.9286 | 3855.6966 | 3900.57
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 139 | 2867 | 15327
2 | GCV ( ADB ) | Kcal/kg | 4578
WTP Report
1 | DM water Generation | m3 | 15 | 270 | 1703
2 | DM water Consumption | m3 | 15 | 269 | 1717
3 | CT Makeup Water Consumption | m3 | 18 | 404 | 2186
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.5 | 1358
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 0 | 351 | 2509
6 | Fly ash to Coal yard(Truck) | nos | 5 | 58 | 274
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 21
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-21 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 177400 | 3570100 | 17890065
2 | Auxiliary power consumption | kWhr | 17627 | 371300 | 1973895
3 | Net Power Exported | kWhr | 159773 | 3198800 | 15916170
4 | Auxiliary power consumption | ( % ) | 9.9363 | 10.4003 | 11.0335
5 | Average Power Generation | MWhr | 7.3917 | 7.0835 | 6.7063
6 | Plant Running Hours | Hrs | 24 | 504 | 2667.66
6 | PLF | ( % ) | 73.9167 | 70.8353 | 67.0628
7 | Feed Water consumption | MT | 812 | 16417 | 83417
8 | Boiler Steam Generation | MT | 790 | 15951 | 80864
9 | Bleed steam | MT | 58 | 1104 | 5192
10 | Turbine steam consumption | MT | 746 | 14896 | 74522
11 | Condensate Generation | MT | 583 | 11728 | 59612
12 | Auxilairy steam consumption | MT | 17 | 373 | 1988
13 | Specific steam consumption | Kg/Kwhr | 4.2052 | 4.1724 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.75536 | 0.84059 | 0.86422
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2831.9504 | 2810.3997 | 2806.3143
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3842.3236 | 3855.0321 | 3899.9924
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 134 | 3001 | 15461
2 | GCV ( ADB ) | Kcal/kg | 4688
1 | DM water Generation | m3 | 12 | 282 | 1715
2 | DM water Consumption | m3 | 11 | 280 | 1728
3 | CT Makeup Water Consumption | m3 | 18 | 422 | 2204
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1506
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 37 | 388 | 2546
6 | Fly ash to Coal yard(Truck) | nos | 1 | 59 | 275
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 22
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-22 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178300 | 3748400 | 18068365
2 | Auxiliary power consumption | kWhr | 17765 | 389065 | 1991660
3 | Net Power Exported | kWhr | 160535 | 3359335 | 16076705
4 | Auxiliary power consumption | ( % ) | 9.9635 | 10.3795 | 11.0229
5 | Average Power Generation | MWhr | 7.4292 | 7.0992 | 6.7127
6 | Plant Running Hours | Hrs | 24 | 528 | 2691.66
6 | PLF | ( % ) | 74.2917 | 70.9924 | 67.1272
7 | Feed Water consumption | MT | 817 | 17234 | 84234
8 | Boiler Steam Generation | MT | 793 | 16744 | 81657
9 | Bleed steam | MT | 56 | 1160 | 5248
10 | Turbine steam consumption | MT | 743 | 15639 | 75265
11 | Condensate Generation | MT | 585 | 12313 | 60197
12 | Auxilairy steam consumption | MT | 18 | 391 | 2006
13 | Specific steam consumption | Kg/Kwhr | 4.1671 | 4.1722 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.75715 | 0.83662 | 0.86317
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.8368 | 2810.2302 | 2806.3195
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3837.4463 | 3854.1956 | 3899.3752
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 135 | 3136 | 15596
2 | GCV ( ADB ) | Kcal/kg | 4551
WTP Report
1 | DM water Generation | m3 | 15 | 297 | 1730
2 | DM water Consumption | m3 | 14 | 294 | 1742
3 | CT Makeup Water Consumption | m3 | 23 | 445 | 2227
4 | Fly ash combustible/ GCV | % / kcal/kg | 19.1 | 1701
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 435 | 2593
6 | Fly ash to Coal yard(Truck) | nos | 0 | 59 | 275
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 23
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-23 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 189400 | 3937800 | 18257765
2 | Auxiliary power consumption | kWhr | 18102 | 407167 | 2009762
3 | Net Power Exported | kWhr | 171298 | 3530633 | 16248003
4 | Auxiliary power consumption | ( % ) | 9.5576 | 10.34 | 11.0077
5 | Average Power Generation | MWhr | 7.8917 | 7.1337 | 6.7231
6 | Plant Running Hours | Hrs | 24 | 552 | 2715.66
6 | PLF | ( % ) | 78.9167 | 71.337 | 67.2314
7 | Feed Water consumption | MT | 859 | 18093 | 85093
8 | Boiler Steam Generation | MT | 838 | 17582 | 82495
9 | Bleed steam | MT | 61 | 1221 | 5309
10 | Turbine steam consumption | MT | 788 | 16427 | 76053
11 | Condensate Generation | MT | 619 | 12932 | 60816
12 | Auxilairy steam consumption | MT | 18 | 409 | 2024
13 | Specific steam consumption | Kg/Kwhr | 4.1605 | 4.1716 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.75502 | 0.8327 | 0.86204
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2801.9219 | 2809.8306 | 2806.2739
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3817.548 | 3852.4329 | 3898.5264
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 143 | 3279 | 15739
2 | GCV ( ADB ) | Kcal/kg | 4684
WTP Report
1 | DM water Generation | m3 | 11 | 308 | 1741
2 | DM water Consumption | m3 | 12 | 306 | 1754
3 | CT Makeup Water Consumption | m3 | 60 | 505 | 2287
4 | Fly ash combustible/ GCV | % / kcal/kg | 18 | 1360
5 | Fly ash to cement mill | MT | 48 | 483 | 2641
6 | Fly ash to Coal yard(Truck) | nos | 0 | 59 | 275
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 24
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-24 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 193700 | 4131500 | 18451465
2 | Auxiliary power consumption | kWhr | 18171 | 425338 | 2027933
3 | Net Power Exported | kWhr | 175529 | 3706162 | 16423532
4 | Auxiliary power consumption | ( % ) | 9.381 | 10.295 | 10.9906
5 | Average Power Generation | MWhr | 8.0708 | 7.1727 | 6.7349
6 | Plant Running Hours | Hrs | 24 | 576 | 2739.66
6 | PLF | ( % ) | 80.7083 | 71.7274 | 67.3495
7 | Feed Water consumption | MT | 875 | 18968 | 85968
8 | Boiler Steam Generation | MT | 851 | 18433 | 83346
9 | Bleed steam | MT | 63 | 1284 | 5372
10 | Turbine steam consumption | MT | 806 | 17233 | 76859
11 | Condensate Generation | MT | 631 | 13563 | 61447
12 | Auxilairy steam consumption | MT | 18 | 427 | 2042
13 | Specific steam consumption | Kg/Kwhr | 4.1611 | 4.1711 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.75374 | 0.829 | 0.86091
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2802.4161 | 2809.483 | 2806.2334
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3790.7086 | 3849.539 | 3897.3945
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 146 | 3425 | 15885
2 | GCV ( ADB ) | Kcal/kg | 4717
WTP Report
1 | DM water Generation | m3 | 13 | 321 | 1754
2 | DM water Consumption | m3 | 13 | 319 | 1767
3 | CT Makeup Water Consumption | m3 | 18 | 523 | 2305
4 | Fly ash combustible/ GCV | % / kcal/kg | 20 | 1497
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 36 | 519 | 2677
6 | Fly ash to Coal yard(Truck) | nos | 1 | 60 | 276
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 25
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-25 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 178800 | 4310300 | 18630265
2 | Auxiliary power consumption | kWhr | 17983 | 443321 | 2045916
3 | Net Power Exported | kWhr | 160817 | 3866979 | 16584349
4 | Auxiliary power consumption | ( % ) | 10.0576 | 10.2852 | 10.9817
5 | Average Power Generation | MWhr | 7.45 | 7.1838 | 6.7412
6 | Plant Running Hours | Hrs | 24 | 600 | 2763.66
6 | PLF | ( % ) | 74.5 | 71.8383 | 67.4116
7 | Feed Water consumption | MT | 815 | 19783 | 86783
8 | Boiler Steam Generation | MT | 793 | 19226 | 84139
9 | Bleed steam | MT | 48 | 1332 | 5420
10 | Turbine steam consumption | MT | 745 | 17978 | 77604
11 | Condensate Generation | MT | 585 | 14148 | 62032
12 | Auxilairy steam consumption | MT | 17 | 444 | 2059
13 | Specific steam consumption | Kg/Kwhr | 4.1667 | 4.1709 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.74944 | 0.8257 | 0.85984
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2806.5157 | 2809.3599 | 2806.2361
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3826.7151 | 3848.5923 | 3896.7162
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 134 | 3559 | 16019
2 | GCV ( ADB ) | Kcal/kg | 4795
WTP Report
1 | DM water Generation | m3 | 15 | 336 | 1769
2 | DM water Consumption | m3 | 14 | 333 | 1781
3 | CT Makeup Water Consumption | m3 | 18 | 541 | 2323
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1380
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 42 | 561 | 2719
6 | Fly ash to Coalyard(Truck) | nos | 0 | 60 | 276
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 26
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-26 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 179300 | 4489600 | 18809565
2 | Auxiliary power consumption | kWhr | 17937 | 461258 | 2063853
3 | Net Power Exported | kWhr | 161363 | 4028342 | 16745712
4 | Auxiliary power consumption | ( % ) | 10.0039 | 10.2739 | 10.9724
5 | Average Power Generation | MWhr | 7.4708 | 7.1949 | 6.7474
6 | Plant Running Hours | Hrs | 24 | 624 | 2787.66
6 | PLF | ( % ) | 74.7083 | 71.9487 | 67.4744
7 | Feed Water consumption | MT | 811 | 20594 | 87594
8 | Boiler Steam Generation | MT | 793 | 20019 | 84932
9 | Bleed steam | MT | 57 | 1389 | 5477
10 | Turbine steam consumption | MT | 744 | 18722 | 78348
11 | Condensate Generation | MT | 583 | 14731 | 62615
12 | Auxilairy steam consumption | MT | 18 | 462 | 2077
13 | Specific steam consumption | Kg/Kwhr | 4.1495 | 4.1701 | 4.1653
14 | Specific fuel consumption | Kg/Kwhr | 0.75293 | 0.82279 | 0.85882
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2794.7685 | 2808.7772 | 2806.1268
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3816.0439 | 3847.2924 | 3895.9472
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 135 | 3694 | 16154
2 | GCV ( ADB ) | Kcal/kg | 4588
WTP Report
1 | DM water Generation | m3 | 15 | 351 | 1784
2 | DM water Consumption | m3 | 13 | 346 | 1794
3 | CT Makeup Water Consumption | m3 | 18 | 559 | 2341
4 | Fly ash combustible/ GCV | % / kcal/kg | 17 | 1300
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 47 | 608 | 2766
6 | Fly ash to Coalyard(Truck) | nos | 0 | 60 | 276
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 27
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-27 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 190700 | 4680300 | 19000265
2 | Auxiliary power consumption | kWhr | 18011 | 479269 | 2081864
3 | Net Power Exported | kWhr | 172689 | 4201031 | 16918401
4 | Auxiliary power consumption | ( % ) | 9.4447 | 10.2401 | 10.957
5 | Average Power Generation | MWhr | 7.9458 | 7.2227 | 6.7577
6 | Plant Running Hours | Hrs | 24 | 648 | 2811.66
6 | PLF | ( % ) | 79.4583 | 72.2269 | 67.5767
7 | Feed Water consumption | MT | 860 | 21454 | 88454
8 | Boiler Steam Generation | MT | 839 | 20858 | 85771
9 | Bleed steam | MT | 63 | 1452 | 5540
10 | Turbine steam consumption | MT | 792 | 19514 | 79140
11 | Condensate Generation | MT | 620 | 15351 | 63235
12 | Auxilairy steam consumption | MT | 18 | 480 | 2095
13 | Specific steam consumption | Kg/Kwhr | 4.1531 | 4.1694 | 4.1652
14 | Specific fuel consumption | Kg/Kwhr | 0.75511 | 0.82003 | 0.85778
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2796.9376 | 2808.2948 | 2806.0345
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3796.0483 | 3845.2044 | 3894.9445
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 144 | 3838 | 16298
2 | GCV ( ADB ) | Kcal/kg | 4730
WTP Report
1 | DM water Generation | m3 | 10 | 361 | 1794
2 | DM water Consumption | m3 | 12 | 358 | 1806
3 | CT Makeup Water Consumption | m3 | 18 | 577 | 2359
4 | Fly ash combustible/ GCV | % / kcal/kg | 19 | 1331
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 40 | 648 | 2806
6 | Fly ash to Coalyard(Truck) | nos | 1 | 61 | 277
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 28
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-28 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 171200 | 4851500 | 19171465
2 | Auxiliary power consumption | kWhr | 17777 | 497046 | 2099641
3 | Net Power Exported | kWhr | 153423 | 4354454 | 17071824
4 | Auxiliary power consumption | ( % ) | 10.3838 | 10.2452 | 10.9519
5 | Average Power Generation | MWhr | 7.1333 | 7.2195 | 6.7608
6 | Plant Running Hours | Hrs | 24 | 672 | 2835.66
6 | PLF | ( % ) | 71.3333 | 72.1949 | 67.6085
7 | Feed Water consumption | MT | 801 | 22255 | 89255
8 | Boiler Steam Generation | MT | 765 | 21623 | 86536
9 | Bleed steam | MT | 52 | 1504 | 5592
10 | Turbine steam consumption | MT | 718 | 20232 | 79858
11 | Condensate Generation | MT | 571 | 15922 | 63806
12 | Auxilairy steam consumption | MT | 18 | 498 | 2113
13 | Specific steam consumption | Kg/Kwhr | 4.1939 | 4.1703 | 4.1655
14 | Specific fuel consumption | Kg/Kwhr | 0.7535 | 0.81769 | 0.85685
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2825.3154 | 2808.8954 | 2806.2067
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3855.4772 | 3845.5669 | 3894.5921
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 129 | 3967 | 16427
2 | GCV ( ADB ) | Kcal/kg | 4750
WTP Report
1 | DM water Generation | m3 | 17 | 378 | 1811
2 | DM water Consumption | m3 | 16 | 374 | 1822
3 | CT Makeup Water Consumption | m3 | 18 | 595 | 2377
4 | Fly ash combustible/ GCV | % / kcal/kg | 22.23 | 1676
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 44 | 692 | 2850
6 | Fly ash to Coalyard(Truck) | nos | 0 | 61 | 277
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 29
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-29 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 187800 | 5039300 | 19359265
2 | Auxiliary power consumption | kWhr | 18189 | 515235 | 2117830
3 | Net Power Exported | kWhr | 169611 | 4524065 | 17241435
4 | Auxiliary power consumption | ( % ) | 9.6853 | 10.2243 | 10.9396
5 | Average Power Generation | MWhr | 7.825 | 7.2404 | 6.7698
6 | Plant Running Hours | Hrs | 24 | 696 | 2859.66
6 | PLF | ( % ) | 78.25 | 72.4037 | 67.6978
7 | Feed Water consumption | MT | 849 | 23104 | 90104
8 | Boiler Steam Generation | MT | 830 | 22453 | 87366
9 | Bleed steam | MT | 65 | 1569 | 5657
10 | Turbine steam consumption | MT | 786 | 21018 | 80644
11 | Condensate Generation | MT | 609 | 16531 | 64415
12 | Auxilairy steam consumption | MT | 18 | 516 | 2131
13 | Specific steam consumption | Kg/Kwhr | 4.1853 | 4.1708 | 4.1657
14 | Specific fuel consumption | Kg/Kwhr | 0.7508 | 0.81519 | 0.85582
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2818.4665 | 2809.2521 | 2806.3257
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3813.3175 | 3844.3651 | 3893.8037
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 141 | 4108 | 16568
2 | GCV ( ADB ) | Kcal/kg | 4546
WTP Report
1 | DM water Generation | m3 | 9 | 387 | 1820
2 | DM water Consumption | m3 | 11 | 385 | 1833
3 | CT Makeup Water Consumption | m3 | 21 | 616 | 2398
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.31 | 1392
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 50 | 742 | 2900
6 | Fly ash to Coalyard(Truck) | nos | 0 | 61 | 277
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 30
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-30 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 186800 | 5226100 | 19546065
2 | Auxiliary power consumption | kWhr | 17875 | 533110 | 2135705
3 | Net Power Exported | kWhr | 168925 | 4692990 | 17410360
4 | Auxiliary power consumption | ( % ) | 9.5691 | 10.2009 | 10.9265
5 | Average Power Generation | MWhr | 7.7833 | 7.2585 | 6.7782
6 | Plant Running Hours | Hrs | 24 | 720 | 2883.66
6 | PLF | ( % ) | 77.8333 | 72.5847 | 67.7821
7 | Feed Water consumption | MT | 845 | 23949 | 90949
8 | Boiler Steam Generation | MT | 826 | 23279 | 88192
9 | Bleed steam | MT | 66 | 1635 | 5723
10 | Turbine steam consumption | MT | 778 | 21796 | 81422
11 | Condensate Generation | MT | 605 | 17136 | 65020
12 | Auxilairy steam consumption | MT | 18 | 534 | 2149
13 | Specific steam consumption | Kg/Kwhr | 4.1649 | 4.1706 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.74946 | 0.81284 | 0.8548
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2804.8929 | 2809.0963 | 2806.312
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3815.2556 | 3843.3246 | 3893.053
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 140 | 4248 | 16708
2 | GCV ( ADB ) | Kcal/kg | 4522
WTP Report
1 | DM water Generation | m3 | 11 | 398 | 1831
2 | DM water Consumption | m3 | 12 | 397 | 1845
3 | CT Makeup Water Consumption | m3 | 18 | 634 | 2416
4 | Fly ash combustible/ GCV | % / kcal/kg | 18.72 | 1396
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 48 | 790 | 2948
6 | Fly ash to Coalyard(Truck) | nos | 0 | 61 | 277
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0

## 31
1*10 MW CAPTIVE POWER PLANT
Daily,Monthly & Yearly Generation Report (FRM-LCL-PP-06)
Sr. NO. | Description | Unit | 2026-07-31 | Month to Date | Year to Date(APR2026-MAR2027)
1 | Gross Power Generation | kWhr | 180300 | 5406400 | 19726365
2 | Auxiliary power consumption | kWhr | 17840 | 550950 | 2153545
3 | Net Power Exported | kWhr | 162460 | 4855450 | 17572820
4 | Auxiliary power consumption | ( % ) | 9.8946 | 10.1907 | 10.9171
5 | Average Power Generation | MWhr | 7.5125 | 7.2667 | 6.7843
6 | Plant Running Hours | Hrs | 24 | 744 | 2907.66
6 | PLF | ( % ) | 75.125 | 72.6667 | 67.8427
7 | Feed Water consumption | MT | 824 | 24773 | 91773
8 | Boiler Steam Generation | MT | 796 | 24075 | 88988
9 | Bleed steam | MT | 57 | 1692 | 5780
10 | Turbine steam consumption | MT | 751 | 22547 | 82173
11 | Condensate Generation | MT | 593 | 17729 | 65613
12 | Auxilairy steam consumption | MT | 0 | 534 | 2149
13 | Specific steam consumption | Kg/Kwhr | 4.1653 | 4.1704 | 4.1656
14 | Specific fuel consumption | Kg/Kwhr | 0.7543 | 0.81089 | 0.85388
15 | Heat Rate(TG)2880 | Kcal/Kwh | 2805.2302 | 2808.9673 | 2806.3021
16 | Heat Rate ( Plant ) 3300 @ MCR | Kcal/Kwh | 3809.2353 | 3842.1877 | 3892.2869
17 | DG Power Generation | kWhr | 0 | 0 | 1468
FUEL Report
1 | Coal Consumption | MT | 136 | 4384 | 16844
2 | GCV ( ADB ) | Kcal/kg | 4768
WTP Report
1 | DM water Generation | m3 | 12 | 410 | 1843
2 | DM water Consumption | m3 | 12 | 409 | 1857
3 | CT Makeup Water Consumption | m3 | 17 | 651 | 2433
4 | Fly ash combustible/ GCV | % / kcal/kg | 21 | 1668
FLY ASH DISPOSAL REPORT
5 | Fly ash to cement mill | MT | 1 | 791 | 2949
6 | Fly ash to Coalyard(Truck) | nos | 32 | 93 | 309
7 | Fly ash to Dumpyard(Truck) | nos | 0 | 0 | 0